## 2023 Redline Version All Commen
Classification | Housing Type | Section | Existing Title | Existing specification | Existing Objective language | Public Comment Justification/substantiation | Committee Adjudication (drop down list) | Committee Rationale for Decision | Revised Proposed Title | Revised Proposed Specification(s) | Revised Proposed Objective(s)
2.0101.2a | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Health and Safety | Selection | Select battery-operated smoke alarms that are listed and labeled in accordance with UL 217 and have sealed, non-replaceable, 10-year batteries | Ensure proper equipment selection | There will be no working smoke detectors in income qualified housing after 10 years. Our clients will not pay $45 for new detector. They will pay for new batteries. | Rejected | Smoke alarms sensors have a lifespan, typically 10-years. Leaving batteries in smoke detectors that are not working does no good. | N/A | N/A | N/A
2.0102.1a | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Health and Safety | Selection | Select CO alarms that are listed and labeled in accordance with UL 2034, or approved by the authority having jurisdiction, and have a minimum of: 10-year manufacturer's warranty Contain internal non-replaceable batteries | Ensure proper equipment selection | This requirement will ensure that there are no working smoke/CO detectors in income qualified housing after 10 years. Income qualified home owners will not spend $45 on smoke/CO detector. They will spend a few dollars for new batteries. | Rejected | CO alarms sensors have a lifespan, typically less than 10-years. Leaving batteries in CO detectors that are not working does no good. Requiring a 10-year warranty extends the life from typical 5-7 of existing units. | N/A | N/A | N/A
2.0103.1c | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Health and Safety | Discharge | Install discharge tube of temperature and pressure relief valve so that it: Discharges to a readily observable location either 6 inches or less from the floor or overflow pan or to the outdoors Discharges in a manner that does not cause personal injury or structural damage Flows by gravity and without any trap Is not directly connected to the dwelling drainage system Does not contain any valves or tees, nor end with a threaded connection | Ensure proper discharge location | Consistency with 7.0302.1f would be appreciated here | Rejected | Adopted this language into 7.0302.1f from this spec for better alignment. | N/A | N/A | N/A
2.0202.2c | Single Family Site-Built Housing, Multifamily Housing | Health and Safety | Coverage | Cover all exposed soil Extend ground vapor retarder a minimum of 6" up all foundation walls and piers, but do not install in contact with non-treated structural wood | Create a continuous ground vapor retarder layer that does not compromise wooden foundation materials | There is little gained by extending the vapor barrier up the walls an foundation piers if it is not to be sealed tight, so striking this language saves time and effort. | Accepted | Use this verbiage to address both requests for this spec change. | Cover all exposed soil. Extend ground vapor retarder a minimum of 6" up all foundation walls and piers, but do not install in contact with non-treated structural wood Do not install in contact with non-treated structural wood. | N/A | N/A
2.0202.2c | Single Family Site-Built Housing, Multifamily Housing | Health and Safety | Coverage | Cover all exposed soil Extend ground vapor retarder a minimum of 6" up all foundation walls and piers, but do not install in contact with non-treated structural wood | Create a continuous ground vapor retarder layer that does not compromise wooden foundation materials | In this instance the floor will be the thermal and pressure boundary. if moisture were to get into the sub space running the vapor barrier up the foundation walls could trap moisture on top at edges which then could migrate into the home | Accepted with modifications | Addresses the same issue as the above suggestion. Accept with modifications and use verbiage from above. | Cover all exposed soil. Extend ground vapor retarder a minimum of 6" up all foundation walls and piers, but do not install in contact with non-treated structural wood Do not install in contact with non-treated structural wood. | N/A | N/A
2.0202.2g | Single Family Site-Built Housing, Multifamily Housing | Health and Safety | Air sealing | Seal all penetrations in the ground vapor retarder with a compatible sealant | Ensure ground vapor retarder is air tight | There is no need for an airtight vapor barrier in a vented space, this change would save time and effort. Additionally, there is no requirement to seal the vapor barrier at the foundation walls or piers in a vented foundation per the current SWS version, so there is no need to seal the penetrations either. | Accepted | The committee agrees this detail should be removed from SWS | This detail is planned for removal | This detail is planned for removal | This detail is planned for removal
2.0202.3b | Single Family Site-Built Housing, Manufactured Housing | Health and Safety | Coverage | Cover all exposed soil Extend ground vapor retarder a minimum of 6" up all foundation walls and piers, but do not install in contact with non-treated structural wood | Create a continuous ground vapor retarder layer that does not compromise wooden foundation materials | It seems unnecessary and cumbersome to extend vapor barrier up foundation walls and piers in a foundation that is very well vented, as would be the case in MH's especially. Suggest striking this portion and just leaving the rest as that meets the objective. | Accepted | Use this verbiage to address both requests for this spec change. | Cover all exposed soil Extend ground vapor retarder a minimum of 6" up all foundation walls and piers, but do Do not install in contact with non-treated structural wood | N/A | N/A
2.0202.3b | Single Family Site-Built Housing, Manufactured Housing | Health and Safety | Coverage | Cover all exposed soil Extend ground vapor retarder a minimum of 6" up all foundation walls and piers, but do not install in contact with non-treated structural wood | Create a continuous ground vapor retarder layer that does not compromise wooden foundation materials | Skirting can not be considered a permanent foundation wall and is by design installable and removable. Accessing the space under the manufactured home or repairing skirting could damage the vapor barrier. If moisture where to get on the vapor barrier it could cause a pooling condition at the edges with no place to run off and possible minimal drying potential | Accepted with modifications | Addresses the same issue as the above suggestion. Accept with modifications and use verbiage from above. | Cover all exposed soil Extend ground vapor retarder a minimum of 6" up all foundation walls and piers, but do Do not install in contact with non-treated structural wood | N/A | N/A
2.0301.2c | Single Family Site-Built Housing, Multifamily Housing | Health and Safety | Clearance | Maintain a minimum of 3" of clearance around live knob and tube wiring | Prevent fire hazards | Need to change spec lettering to "a". This was a typo in the original import and can be corrected at any time. | Accepted | Typo in spec lettering, simple fix. No need to further review. | Lettering of spec was fixed on SWS site | Lettering of spec was fixed on SWS site | Lettering of spec was fixed on SWS site
2.0301.2d | Single Family Site-Built Housing, Multifamily Housing | Health and Safety | Marking | Mark all live knob-and-tube wiring with caution tape that is visible from at least 5' away and post appropriate signage | Provide essential safety and maintenance information and maintain safe operation of knob-and-tube wiring | Need to change spec lettering to "b". This was a typo in the original import and can be fixed at any time. | Accepted | Typo in spec lettering, simple fix. No need to further review. | Lettering of spec was fixed on SWS site | Lettering of spec was fixed on SWS site | Lettering of spec was fixed on SWS site
3.0103.1e | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Air Sealing | Seal access panel | Seal access using gaskets, weather stripping or equivalent method Permanently attach gaskets, weatherstripping, etc. per manufacturer's instructions Secure attic door or hatch with a latch, lock or frictionally engaging components | Prevent air and moisture movement | This groups attic access lids and knee wall access doors into the same category. The weight of the now insulated and weatherstripped attic access lid should be sufficient enough to seal. | Reject | This concept is covered by "frictionally engaging components". No change recommended. | N/A | N/A | N/A
3.0201.1i | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Air Sealing | Safety | Verify safe operation and size of egress windows as required by local codes | Safe egress maintained | Verifying proper size of egress windows presumes it is the responsibility of weatherization workers to replace such windows if found to be non-compliant for egress. | Accept with modifications | This spec is related to ensuring the safety of the client, and does not require the replacement of non-compliant windows, however it does steer towards dictating the process rather than the installation. We want all windows to operate safely not just egress. Listing egress implies WAP would bring window size to code which is not the intent of the SWS and is a local agency decision. | N/A | Verify safe operation and size of egress windows as required by local codes | Safe egress operation maintained
3.0202.1a | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Air Sealing | Sealant selection | Select sealants that: are compatible with their intended surfaces, allow for differential expansion and contraction between dissimilar materials, meet the requirements of the applicable fire safety code (e.g., thermal or ignition barriers), and for use inside the pressure boundary select low volatile organic compound (VOC) sealants that meet independent testing and verification protocols | Select safe and effective sealants | I have 2 doors that I can see light in the seams of and there is a large draft coming in. | Reject | Not an actual comment, but is a request from a client for services. | N/A | N/A | N/A
4.0102.1c | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Insulation | Material selection | Select insulation materials that have a flame spread and smoke development index of 75/450 or less when tested in accordance with ASTM E84 or UL 723 | Select fire safe insulation | From building science.com. https://www.buildingscience.com/documents/reports/rr-0912-spray-polyurethane-foam-need-for-vapor-retarders-in-above-grade-walls/view More specifically, the research concluded* that: Closed-cell (about 2 pounds per cubic foot density or more) spray foam applied in thicknesses of over 2" (50 mm) will control vapor diffusion to safe levels in all climates up to 10000 HDD and interior winter-time relative humidities of up to an over 50%RH. As thickness increases the level of diffusion control increases. The diffusion control is equivalent to walls with the traditional fiberglass batt and polyethylene. Open cell (1/2 pound per cubic foot density) foam can control diffusion in climates that are not too cold (e.g. under 4500 HDD) and when the interior winter RH level is controlled by appropriate ventilation to below about 40%. Open cell foam does not have sufficient vapor control for use in very cold climates (4500 HDD to 5000 HDD) unless the interior winter-time RH is strictly controlled (to below about 30%RH). For either type of foam, the wood framing provides sufficient inherent vapor resistance to maintain the moisture content within the safe range even in very cold exterior climates (10 000 HDD) and very humid interior conditions (50%RH in winter). | Accept with modifications | The research linked applies to exterior walls, not attics. In attics the thickness of the insulation is sufficient in nearly all cases to stop vapor diffusion, and additional ignition barriers will also accomplish the same thing without limiting the type of insulation to be used. If anything, require that the insulation have a certain vapor perm rating in cold climates. In the field, roof leaks are far more problematic than vapor diffusion and no contractors in our region would install closed cell on a roof deck for that reason. The R value installed should inhibit moisture diffusion and specifying closed cell foam could be problematic if a roof leak occurred.Foam 6-8 inches will meet class 2 vapor retarder requirements. | N/A | Select insulation materials that do not exceed a perm rating of 2 and have a flame spread and smoke development index of 75/450 or less when tested in accordance with ASTM E84 or UL 723 | N/A
4.0104.2a | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Insulation | Pre-work qualifications | Verify that installation area is free of: active water leaks, fuel leaks (i.e., gas, oil, propane), and pest intrusions energized knob and tube wiring uncovered electrical junctions improperly terminated devices (ventilation fans, dryers, plumbing stacks, condensate lines, combustion appliance flues/chimneys, etc.) unshielded high-temperature devices (non-IC rated recessed lights, chimneys, flues, vents, etc.) unless they are zero clearance devices insulation escape openings Verify that installation area is: intact, able to support insulation weight, and air sealed (including blockers under kneewalls in alignment with the interior side of the kneewall) | Prepare for safe, effective, and airtight installation of dense-packed insulation | cut and paste error from the dense-packed wall insulation spec that was carried forward. This spec does not address dense-packed insulation but instead is related to batt insulation of knee walls. | Accept | Just a typo. | N/A | N/A | Prepare for safe, effective, and airtight installation of knee wall batt insulation.
4.0104.2e | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Insulation | Install backing | Install airtight backing material in full contact with the existing cavity insulation Secure backing material using mechanical fasteners that penetrate the sub framing a minimum of 1" Installation must have a minimum of a 30-year service life | Airtight, and durable insulation cavity | This specification is not needed. If this is needed why not install airtight backing to the entire attic insulation? It doesn't make sense for the relatively low energy savings. If so please show me a study on the energy savings for this. In addition, if NREL wants to do this they need to give way more direction on what an "air tight" backing material is. Can you use 6 mil poly? In my climate zone that would be a bad idea because it would trap vapor inside the wall cavity. | Accepted with modifications | The backing of knee walls with an air barrier is required by the IRC, Energy Star, and most all above code building standards. https://basc.pnnl.gov/resource-guides/attic-knee-walls This addresses attic knee wall insulation, which should have an air-tight barrier on both sides to be effective due to the vertical position of the insulation vs. horizontal installations on the attic floor. Clarifying that vapor permeable material cover the insulation will prevent such things as poly being used which could trap moisture. | N/A | Install an airtight vapor permeable backing material in full contact with the existing cavity insulation Secure backing material using mechanical fasteners that penetrate the sub framing a minimum of 1" Installation must have a minimum of a 30-year service life | Airtight, vapor permeable, and durable insulation cavity protection
4.0202.1a | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Insulation | Pre-work qualifications | Verify that installation area is free of: active water leaks, fuel leaks (i.e., gas, oil, propane), and pest intrusions energized knob and tube wiring improperly terminated devices (ventilation fans, dryers, plumbing stacks, condensate lines, combustion appliance flues/chimneys, supply and/or return air, etc.) unshielded high-temperature devices (non-IC rated recessed lights, chimneys, flues, vents, etc.) unless they are zero clearance devices insulation escape openings Verify that installation area is: intact and able to support insulation weight and pressure | Prepare for safe, effective, and airtight installation of dense-packed insulation | good | Rejected | No actual change suggested. | N/A | N/A | N/A
4.0301.6c | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Insulation | General preparation | Remove any existing insulation or vapor barrier materials from installation area Install airtight blocking between each floor joist at the interior edge of the exterior wall plate | Prevent condensation, prevent air and moisture movement in attached floor cavities | I'm on disability I can't do the work myself | Rejected | Not an actual comment, but is a request from a client for services. | N/A | N/A | N/A
4.0401.3d | Single Family Site-Built Housing, Multifamily Housing | Insulation | Batt installation | Install rigid insulation to prescribed R-value in every joist bay in full contact with the rim/band joist air barrier and all sides of the cavity without gaps, voids, or misalignments | Continuous and contiguous thermal boundary | This reference is for rigid insulation, not batts. | Accepted | We concur with the suggested change. This is a simple verbiage change with no impact on installations. | Insulation installation | N/A | N/A
4.0402.1b | Single Family Site-Built Housing, Multifamily Housing | Insulation | Material selection | Select insulation that: has a flame spread/smoke development index of 25/450 or less when tested in accordance with ASTM E 84 or UL 723 is, or include a facing that is, a class II vapor retarder is non-absorbent | Select fire safe and moisture resistant materials | Align specification language with that found in 4.0402.4b and 4.0402.5b for consistence | Accepted with modifications | Regardless of Appendix A which doesn't specify where the insulation types are to be installed, this is about preventing moist air from moving from inside a conditioned space to the exterior surface and condensing. Previously, the committees debated whether or not any drying to the inside was desirable and determined the answer was no. The other specs mentioned in the justification are relating to conditioned basements, which typically have more connection to the main body of the house, and are better conditioned. | N/A | Select insulation that: has a flame spread/smoke development index of 25/450 or less when tested in accordance with ASTM E 84 or UL 723 is, or include a facing that is, a class II vapor retarder is non-absorbent not water absorbent | Select fire safe and moisture resistant materials hydrophobic materials
4.0402.1b | Single Family Site-Built Housing, Multifamily Housing | Insulation | Material selection | Select insulation that: has a flame spread/smoke development index of 25/450 or less when tested in accordance with ASTM E 84 or UL 723 is, or include a facing that is, a class II vapor retarder is non-absorbent | Select fire safe and moisture resistant materials | The language as it is written excludes items in 10 CFR 440 Appendix A like mineral and cellulosic board insulation. These materials generally do not have a vapor retarder and are vapor permeable allowing for drying potential to the interior. facing can trap moisture in between the foundation and these now excluded materials. | Accepted with Modifications | Regardless of Appendix A which doesn't specify where the insulation types are to be installed, this is about preventing moist air from moving from inside a conditioned space to the exterior surface and condensing. Previously, the committees debated whether or not any drying to the inside was desirable and determined the answer was no. | N/A | Select insulation that: has a flame spread/smoke development index of 25/450 or less when tested in accordance with ASTM E 84 or UL 723 is, or include a facing that is, a class II vapor retarder is non-absorbent not water absorbent | Select fire safe and moisture resistant materials hydrophobic materials
4.0402.1e | Single Family Site-Built Housing, Multifamily Housing | Insulation | Installation | Install insulation to prescribed R-value in full contact with the foundation wall from ceiling to floor with vapor retarder facing the conditioned space | Contiguous and continuous thermal barrier | The energy audit will specify the area to be covered per the measure selection process. The SWS should not dictate the measure selection (i.e., the area to be covered) but only the installation method. | Accept | This addresses the same issue as comments made in 4.0402.4e. | N/A | Install insulation to prescribed R-value in full contact with the foundation wall from ceiling to floor with vapor retarder facing the conditioned space | N/A
4.0402.2f | Single Family Site-Built Housing, Multifamily Housing | Insulation | Installation | Install insulation to prescribed R-value in a continuous layer in full contact with the foundation wall from ceiling to floor If installing multiple layers, offset seams by a minimum of 12" and seal the seams and joints of each layer before installing the next layer | Contiguous and continuous thermal barrier | The energy audit will specify the area to be covered per the measure selection process. The SWS should not dictate the measure selection (i.e., the area to be covered) but only the installation method. | Accept | This addresses the same issue as comments made in 4.0402.4e. | N/A | Install insulation to prescribed R-value in a continuous layer in full contact with the foundation wall from ceiling to floor If installing multiple layers, offset seams by a minimum of 12" and seal the seams and joints of each layer before installing the next layer | N/A
4.0402.3f | Single Family Site-Built Housing, Multifamily Housing | Insulation | Installation | Install insulation to prescribed R-value in a continuous layer in full contact with the foundation wall from ceiling to floor using a pass thickness maximum in accordance with manufacturer specifications Install SPF to a thickness of at least a class II vapor retarder | Continuous thermal barrier which prevents air and moisture vapor movement | The energy audit will specify the area to be covered per the measure selection process. The SWS should not dictate the measure selection (i.e., the area to be covered) but only the installation method. | Accepted | This addresses the same issue as comments made in 4.0402.4e. | N/A | Install insulation to prescribed R-value in a continuous layer in full contact with the foundation wall from ceiling to wall using a pass thickness maximum in accordance with manufacturer specifications Install SPF to a thickness of at least a class II vapor retarder | N/A
4.0402.4e | Single Family Site-Built Housing, Multifamily Housing | Insulation | Installation | Install insulation to prescribed R-value in full contact with the entire perimeter of foundation wall from ceiling to floor If insulation has a vapor retarder on only one side install it facing the conditioned space | Contiguous and continuous thermal barrier | The energy audit will specify the area to be covered per the measure selection process. The SWS should not dictate the measure selection (i.e., the area to be covered) but only the installation method. | Accept | Use this verbiage to address all related requests for changes to this spec. | N/A | Install insulation to prescribed R-value in full contact with the entire perimeter of foundation wall from ceiling to floor If insulation has a vapor retarder on only one side install it facing the conditioned space | N/A
4.0402.4e | Single Family Site-Built Housing, Multifamily Housing | Insulation | Installation | Install insulation to prescribed R-value in full contact with the entire perimeter of foundation wall from ceiling to floor If insulation has a vapor retarder on only one side install it facing the conditioned space | Contiguous and continuous thermal barrier | Often, the cost to insulate the entire wall drives the SIR below 1 and the measure cannot be done in Wx. You can reduce the heat loss in the wall by 90% by insulating down to frost line. It would seem to be better to insulate what you can do cost effectively versus not insulating the wall at all if you have to do it to the floor. | Accepted with modifications | This is a duplicate request for the same spec as above. Suggest we accept the verbiage for the first and acknowledge the change here as well as accepted with modifications. | N/A | Install insulation to prescribed R-value in full contact with the entire perimeter of foundation wall from ceiling to floor If insulation has a vapor retarder on only one side install it facing the conditioned space | N/A
4.0402.5d | Single Family Site-Built Housing, Multifamily Housing | Insulation | Installation | Install insulation to prescribed R-value in a continuous boundary around the entire perimeter of foundation wall from top of band joist to floor, in contact with any waterproof membrane that exists at the foundation wall | Contiguous and continuous thermal barrier | The energy audit will specify the area to be covered per the measure selection process. The SWS should not dictate the measure selection (i.e., the area to be covered) but only the installation method. | Accept | This addresses the same issue as below. | N/A | Install insulation to prescribed R-value in a continuous boundary around the entire perimeter of foundation wall from top of band joist to floor, in contact with any waterproof membrane that exists at the foundation wall | N/A
5.0106.3a | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Heating and Cooling | Material selection | Select sealant that is UL 181 approved | Select safe and effective sealant | AeroSeal, the leading product in this category is UL listed under UL 1381, which is specific to it's properties, but is not UL 181 listed. Removal of the specific "UL 181" removes potential roadblocks to the adoption of new technologies into the industry. | Accept | Suggest accepting, simple change to acknowledge changing materials. | N/A | Select sealant that is UL 181 approved | N/A
6.0101.1a | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Ventilation | Material selection | Select duct materials that have a flame spread no greater than 25 Select flexible ducts that are UL 181 listed or Air Diffusion Council approved Select rigid ducts of 28 gauge or thicker Select duct insulation with a flame spread/smoke development index of 25/50 or less when tested according to ASTM E84 or UL 723 | Select durable, safe, and effective duct materials | 28 gauge is not commonly available in all areas of the country. | Reject | Do not concur with using less than 28 gauge metal duct. The IRC allows up to 29 gauge for galvanized, but no less than 26 for aluminum ducts. Suggest rejecting this change as it strikes a balance between the two material types already. | N/A | N/A | N/A
6.0101.1d | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Ventilation | Mechanical fastening | Fasten all ducts as follows: Round metal-to-metal or metal-to-PVC with a minimum of three equally spaced screws For other metal-to-metal or metal-to-PVC with welds, gaskets, mastics (adhesives), mastic-embedded-fabric systems, or tapes Flexible duct-to-metal or flexible duct-to-PVC with tie bands using a tie band tensioning tool PVC-to-PVC materials with approved PVC primer and cement Fasten other specialized duct fittings in accordance with manufacturer specifications | Durable duct connections | The screws can prevent the fan's damper from operating or opening properly. This requirement conflicts with manufacturers instructions. | Rejected | No actual change was made in the spec in "proposed specification". This SWS applies to the ducting, not the fan installation, nor does it address the connection to the fan housing at all. Perhaps adding a mention of ensuring that duct to fan housing connections do not interfere with damper operation would be helpful in the fan installation sections in 6.0201.1c as it is already implied by the objective of that spec. | N/A | Added the following language in red to 6.0201.1c If the fan does not contain an integrated damper, install a damper that: opens in the direction of the desired flow closes when the system is off fan housing connections shall not interfere with damper operation | N/A
6.0201.1a | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Ventilation | Fan selection | Select a fan that: produces no more than 2.0 sones at maximum speed has an efficacy of 4 cfm/watt or more moves at least 50 cfm after installation, ducting, and termination is complete | Select efficient and quiet equipment | ASHRAE 62.2-2016, section 7.2.2 requires 3 sone max for bath or kitchen fans that are used as local exhaust. | Accepted with modifications | Concur with suggested change, but suggest changing the word “produces” to “rated at”. Sones can’t be measure in the field so it is the laboratory rating that is of concern. | N/A | Select a fan that: produces rated as no more than 2.0 sones at maximum speed has an efficacy of 4 cfm/watt or more moves at least 50 cfm after installation, ducting, and termination is complete | N/A
6.0201.1c | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Ventilation | Damper | If the fan does not contain an integrated damper, install a damper that: opens in the direction of the desired flow closes when the system is off | Prevent unwanted air movement while not restricting desired air flow | A comment proposed for spec 6.0101.1c is addressed here, where the Committee decided adding a mention of ensuring that duct to fan housing connections do not interfere with damper operation would be helpful as it is already implied by the objective of this spec. | Accepted | Committee decided adding a mention of ensuring that duct to fan housing connections do not interfere with damper operation would be helpful as it is already implied by the objective of this spec. | N/A | If the fan does not contain an integrated damper, install a damper that: opens in the direction of the desired flow closes when the system is off fan housing connections shall not interfere with damper operation | N/A
6.0202.1a | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Ventilation | Duct selection | Select dryer transition ducting materials that are UL 2158A approved and less than 8 feet in total length with no joints Select primary dryer ducting material that is 28 gauge metal with a smooth interior | Smooth airflow that does not collect lint | Again. 28 gauge is not readily available in all locations of the country. | Accepted with modifications | The committee determined the reference to 28 gauge shall remain because the IRC requires 28 gauge or thicker for all dryer vents (M1502.4.1). The committee determined a need to clarify that transition ducts connect the dryer to the primary exhaust duct | N/A | Transition ducts (flexible or rigid) used to connect the dryer to the primary exhaust duct system shall be UL 2158A approved and less that 8 feet in total length with no joints. Select primary dryer ducting material that is 28 gauge metal with a smooth interior. | N/A
6.0202.1b | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Ventilation | Venting installation | Vent all clothes dryers to the outdoors, which does not include unconditioned spaces such as attics and crawl spaces that are ventilated with the outdoors Choose the shortest practical installation path Install a dryer booster fan that is listed and labeled to UL 705 for dryer ducts exceeding 35' in equivalent length Install ducts according to SWS detail for "Ventilation Ducts" | Dryer ducted to outdoors durably and effectively | A booster fan inline with hot wet lint? This will cause many call backs for private contractors, yay! It will cause unvented dryers for income qualified, Boo! | Accepted with modifications | Interestingly, the IRC has switched the terminology here in the 2021 version (IRC M1502.4.5). They forbid "domestic booster fans", but allow for "domestic exhaust duct power ventilators" that meet UL 705. They also prescriptively limit the length of dryer duct to a maximum of 35 feet equivalent total length though they allow the dryer manufacturer's instructions to supersede this direction which opens the door for the "power ventilators" and longer duct runs. Suggest we remove the booster fan requirement and limit the duct length to 35' equivalent maximum. | N/A | Vent all clothes dryers to the outdoors per manufacturer specifications, which does not include unconditioned spaces such as attics and crawl spaces that are ventilated with the outdoors Choose the shortest practical installation path Install a dryer exhaust duct power ventilator that is listed and labeled to UL 705 for dryer ducts exceeding 35' in equivalent length Install ducts according to SWS detail for "Ventilation Ducts" | N/A
6.0202.1h | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Ventilation | Sealing | Seal all duct connections with 181B or 181B-M listed material | Airtight ducts | ease of product availability | Rejected | After discussion with the author, it appears this was test comment and no suggestions were provided. Author advised that it should be rejected as a test comment. | N/A | N/A | N/A
6.0202.1h | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Ventilation | Sealing | Seal all duct connections with 181B or 181B-M listed material | Airtight ducts | Test | Rejected | Test. Disregard. | N/A | N/A | N/A
6.0202.1h | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Ventilation | Sealing | Seal all duct connections with 181B or 181B-M listed material | Airtight ducts | Test revision. Please disregard. | Rejected | Test. Disregard. | N/A | N/A | N/A
6.0202.1h | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Ventilation | Sealing | Seal all duct connections with 181B or 181B-M listed material | Airtight ducts | Test justification. Please disregard. | Rejected | Test. Disregard. | N/A | N/A | N/A
7.0103.3c | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Baseload | Disposal | Permanently remove equipment from job site and recycle or dispose of removed equipment and refrigerant in accordance with local and federal law (e.g., EPA Section 608 of Clean Air Act of 1990) Permanently decommission old equipment | Old equipment is permanently removed from service, protect the environment, and comply with regulation | EPA Section 608 of the Clean Air Act has to do with refrigerants, which is inappropriate for lighting and ballast removal/disposal. PCBs are dealt with in the Toxic Substance Control Act and Title 40 of the CFR. | Accepted | Concur with suggested change. | N/A | Permanently remove equipment from job site and recycle or dispose of removed equipment and refrigerant ballast in accordance with local and federal law (e.g., EPA Section 608 of Clean Air Act of 1990) (e.g., Part 761 in Title 40 of the Code of Federal Regulations ) Permanently decommission old equipment | N/A
7.0301.2d | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Baseload | Clearance | Maintain a minimum clearance of 6" between combustible tank insulation and fuel-fired water heater draft hood and/or single wall metal vent materials Do not wrap the top of fuel-fired water heaters or cover combustion air intakes | Prevent a fire hazard | Some flue pipe such as B-vent has different clearances. If oil is used to heat water and single wall flue pipe is utilized code requires 18â€ clearance. | Accepted with modifications | Concur with suggestions, but need to reword/reformat a bit. | N/A | Maintain a minimum clearance of 6" or the distance specified by the manufacturer between combustible tank insulation and fuel-fired water heater draft hood and/or single wall metal vent materials. Do not wrap the top of fuel-fired water heaters or cover combustion air intakes | N/A
7.0302.1f | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Baseload | Water Heating | Install a Tempreature and Pressure (TandP) relief valve per the IRC and manufacturer specifications Pipe the valve to within 6' of the floor or drain pan or to the outdoors and must terminate in an observable location Select piping material based on IRC requirements | Direct scalding water away from occupants | The committee requested to change language from this specification to align with 2.0103.1c. | Accepted | Change language to align with 2.0103.1c. | N/A | Install a Tempreature and Pressure (TandP) relief valve per the IRC and manufacturer specifications Pipe the valve to within 6' or less from the floor or drain pan or to the outdoors and must terminate in an observable location Select piping material based on IRC requirements | N/A
7.0302.1f | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Baseload | TandP valve and piping | Install a Temperature and Pressure (TandP) relief valve per the IRC and manufacturer specifications Pipe the valve to within 6" of the floor or drain pan or to the outdoors and must terminate in an observable location Select piping material based on IRC requirements | Direct scalding water away from occupants | Clarity. Some Service Providers following this guidance have understood that they should install between 0" and 6" from the floor. | Accepted with modifications? | Reject the suggested language, but duplicate the language from 2.0103.1c here for consistency. The pipe should be installed from the T&P valve to no greater than 6 inches off the floor. It cannot be more than 6" from the floor per the IRC, nor should it be for occupant safety. | N/A | Install a Tempreature and Pressure (TandP) relief valve per the IRC and manufacturer specifications Pipe the valve to within 6' or less from the floor or drain pan or to the outdoors and must terminate in an observable location Select piping material based on IRC requirements | N/A
7.0302.1f | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Baseload | TandP valve and piping | Install a Temperature and Pressure (TandP) relief valve per the IRC and manufacturer specifications Pipe the valve to within 6" of the floor or drain pan or to the outdoors and must terminate in an observable location Select piping material based on IRC requirements | Direct scalding water away from occupants | IRC P2804.6.1 states that piping cannot terminate above a floor that may be damaged by water. This rule should be maintained by the SWS but as currently worded, does not specify such. | Accepted with modifications? | Duplicate request above, suggest we align the language from 2.0103.1c here as well. | N/A | Install a Tempreature and Pressure (TandP) relief valve per the IRC and manufacturer specifications Pipe the valve to within 6' or less from the floor or drain pan or to the outdoors and must terminate in an observable location Select piping material based on IRC requirements | N/A
7.0302.2b | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Baseload | Equipment selection | Select a system that: is ENERGY STAR certified, equivalent, or better includes a low nitrogen oxide burner fits in the installation space with required clearances provides sufficient hot water for the home and occupants | Select efficient, durable, and properly sized water heater | Energy Star water heaters are impossible to find for MHs, and even in SF storage tank water heaters rarely meet the efficiency requirements of EnergyStar. If left as it currently exists, the SWS essentially mandates on-demand gas water heaters to meet the UEF of EnergyStar. | Accepted | This change should be reflected only for SF and MF. The primary issue is that Energy Star DWH are almost all "on-demand" or instantaneous, rather than storage tank and therefore are cost prohibitive and often not practical for the installation space. Accept. Suggestion to go with .70. | N/A | Select a system that: Is ENERGY STAR certified, equivalent, or better is rated 0.70 UEF or better includes a low nitrogen oxide burner fits in the installation space with required clearances provides sufficient hot water for the home and occupants For Manufactured Housing only: Select a system that: Is listed and labeled for installation in Manufactured Homes draws all its combustion air from outside the dwelling fits in the installation space with required clearances provides sufficient hot water for the home and occupants | Select efficient safe, durable, and properly sized water heater
7.0302.2b | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Baseload | Equipment selection | Select a system that: is ENERGY STAR certified, equivalent, or better includes a low nitrogen oxide burner fits in the installation space with required clearances provides sufficient hot water for the home and occupants | Select efficient, durable, and properly sized water heater | Energy Star certified, or equivalent fuel-fired storage tank DWH that also meet the requirements for installation in MH's are not commercially available. This change should only apply to the MH category. The SF and MF spec remains the same. | Accepted with modifications | There is a need to modify the specification for MH, to remove the energy star requirements and low NOX burner as these are not available for MH. Will need to separate this spec from the others and just leave for MH. | N/A | Select a system that: Is ENERGY STAR certified, equivalent, or better is rated 0.70 UEF or better includes a low nitrogen oxide burner fits in the installation space with required clearances provides sufficient hot water for the home and occupants For Manufactured Housing only: Select a system that: Is listed and labeled for installation in Manufactured Homes draws all its combustion air from outside the dwelling fits in the installation space with required clearances provides sufficient hot water for the home and occupants | Select efficient safe, durable, and properly sized water heater
7.0302.2b | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Baseload | Equipment selection | Select a system that: is ENERGY STAR certified, equivalent, or better includes a low nitrogen oxide burner fits in the installation space with required clearances provides sufficient hot water for the home and occupants | Select efficient, durable, and properly sized water heater | Align with the language in 7.0302.1 that removes reference to Energy Star. | Accepted with modifications | This change should be reflected only for SF and MF, use the suggestion below for MH only. The primary issue is that Energy Star DWH are almost all "on-demand" or instantaneous, rather than storage tank and therefore are cost prohibitive and often not practical for the installation space. Accept. Suggestion to go with .70. | N/A | Select a system that: Is ENERGY STAR certified, equivalent, or better is rated 0.70 UEF or better includes a low nitrogen oxide burner fits in the installation space with required clearances provides sufficient hot water for the home and occupants For Manufactured Housing only: Select a system that: Is listed and labeled for installation in Manufactured Homes draws all its combustion air from outside the dwelling fits in the installation space with required clearances provides sufficient hot water for the home and occupants | Select efficient safe, durable, and properly sized water heater
7.0302.3c | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Baseload | Location | Install appliance where it: is in conditioned space is accessible for service has sufficient volume of air per manufacturer specifications will not affect indoor thermostat readings or blow directly on occupants | Select indoor, safe, and accessible location with sufficient air volume | HPWH can be installed in unconditioned spaces. See: https://basc.pnnl.gov/code-compliance/heat-pump-water-heaters-code-compliance-brief | Accepted with modifications | While they "can" be installed in unconditioned spaces, it is not ideal for efficiency purposes. If installed in a basement space that is unintentionally conditioned, it might be fine, but should not be in truly unconditioned spaces like attics or garages, especially in cold climates. Committee comments are requested. Climate would make a difference on this one. Manufacturer will list a temperature. WE should focus on that. Don't install below a temp. specified by the equipment manufacturer. Similar to sufficient volume language, go with that for temperature. | N/A | Install appliance where it: is in conditioned space Is in a location above the minimum temperature specified by the equipment manufacturer is accessible for service has sufficient volume of air per manufacturer specifications will not affect indoor thermostat readings or blow directly on occupants | N/A

## 2023 Redline Detailed Spec.
Classification | Housing Type | Section | Topic | Subtopic | Detail | Existing Title | Existing Objective language | Status | Submitted | Updated | Submitted By | Proposed Supporting Materials | Public Comment Justification/substantiation | Cost increase | Committee Adjudication (drop down list) | Committee Rationale for Decision | Proposed Spec number change | Revised Proposed Title | Revised Proposed Specification(s) | Revised Proposed Objective(s)
2.0202.1 | Single Family Site-Built Housing, Multifamily Housing | Health and Safety |  |  |  | Un-Vented Subspaces - Ground Cover | Minimize ground moisture vapor and soil gas with a durable, effective vapor retarder | [5 empty] | While rare in warm climates, in very cold climates the subspace under MH's is often brought inside the envelope and should be treated in like manner. | Accepted | Accepted | Concur. Add to MH standards. No change to the details/specs, just adding the housing type.
2.0202.2 | Single Family Site-Built Housing, Multifamily Housing | Health and Safety |  |  |  | Vented Subspaces - Ground Cover | Minimize ground moisture vapor and soil gas with a durable, effective vapor retarder | [5 empty] | While not as common in warm climates, fully enclosed vented foundations under MH's do exist in the field and should be addressed in the same way. | Accepted | Accepted | Concur. Add to MH standards. No change to the detail/specs, just adding the housing type.
2.0301.2 | Single Family Site-Built Housing, Multifamily Housing | Health and Safety |  |  |  | Knob and Tube Wiring - Isolation | Prevent electrocution and reduce fire hazards | [5 empty] | The numbering of the specs in this detail are incorrect. Should start with a and b not c and d. Error in the upload. Need to fix simple error. | Accepted | Accepted | Just a renumbering issue. No committee input necessary. Accept.
3.0102.1 | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Air Sealing |  |  |  | Sealing Non-Insulation Contact (IC) Recessed Light | Airtight, durable, and fire safe enclosure that remains in place and prevents air movement @ 50 Pascals of pressure |  |  |  |  | https://www.prolighting.com/blog/2022/01/20/how-to-choose-led-recessed-lighting/¦Choosing the Best LED Recessed Lighting â€” What You Should Know, https://blog.recessedlighting.com/led-recessed-lights/¦The 3 Best LED Recessed Lights Used By Pros In 2022, https://www.inlineelectric.com/lifespan#:~:text=While%20incandescent%20light%20bulbs%20were,for%20at%20least%2020%20years.¦What is the life span of an LED bulb or light fixture? | This format of LED has a very low failure rate and a very long lifecycle because of its ability to dissipate heat, so is unlikely to need replacement for a good 10 - 20 years. The units are low-cost, easy to install, save on lighting consumption, and are easy to make air-tight with a small bead of caulk around the perimeter after installation. |  | Accepted with modifications | The committee discussed whether they want to add a detail for installing LED retrofit kits w/airtight trim in non-IC rated can lights to accomplish the same outcome as the existing detail for sealing the can light with a box. A new specification for LED retrofits was created and the existing non-IC specification covers instances where a bulb was simple changed from an incandescent to an LED Through committee discussion, additional clarification was added to 3.0102.1c. |  |  | Specification 3.0102.1c Clearance: Maintain a minimum clearance of 3" between enclosure and all portions of fixture (e.g. wiring, box, and ballast) Enclosure must be at least as tall as the surrounding insulation. Note: Installing an LED bulb in a non-IC rated fixture does not change the rating of the fixture or the need for an airtight enclosure.
3.0103.1 | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Air Sealing |  |  |  | Access Doors and Hatches | Attic access door safely and durably sealed and insulated to prevent air movement @ 50 Pascals of pressure | [5 empty] | There is no guidance for the creation of a new attic access, although guidance for a new crawlspace access exists. |  | Rejected | The committee discussed and determined a new specification for new attic access installation was not necessary as the objective for any attic access treatment (new or existing) is to have an air-tight insulated opening. Simply cutting the hole does not warrant SWS guidance and is better handled at the local level (e.g., size requirements, safe work practices, etc.)
3.0202.1 | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Air Sealing |  |  |  | Door Air Sealing | Weathertight door repairs that maintain operability | [5 empty] | I can not afford a new door at this time and do not know how to replace the seal if needed |  | Rejected | Not an actual comment, but is a request from a client for services.
4.0202.6 | Manufactured Housing | Insulation |  |  |  | SPF Insulation Installation in Closed Cavities | Continuous, contiguous, and safe thermal boundary |  |  |  |  | https://www.buildinggreen.com/blog/formaldehyde-based-foam-insulation-back-dead | Foam used for these applications is not spray polyurethane foam. |  | Accepted with modifications | Committee agreed a change to the title is needed as SPF foam injected into an enclosed cavity can cause damage and the existing title SPF was not correct for this application. Committee also determined a need to make a change to the language in specification 4.0202.6b. Not all injected foams are formaldehyde based and adding a requirement that the product not contain formaldehyde and be low expansion foam variety will improve the safety and durability of installations. Since the material specification includes new language, the objective needs to be changed slightly to better align as well. |  | Title: SPF Injection foam Insulation in Enclosed Cavities | Specification 4.0202.6b Material Selection: Select insulation that has a flame spread and smoke development index of 75/450 or less when tested in accordance with ASTM E84 or UL 723 Insulation should be low expansion foam that does not contain formaldehyde. | Objective 4.0202.6b Material Selection: Select fire safe materials
5.0301.1 | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Heating and Cooling |  |  |  | Through-Wall and Window Units | Efficient, safe, and compliant room conditioning |  |  |  |  | http://www.forgreenheat.org/upload/upload/SWS_Proposed%20Specifications-2-%20wood%20stove.pdf | We are proposing a new subsection on wood and pellet stoves and we have it prepared in grid format, like the other sections. The attached supporting materials language has been prepared and endorsed by the Chimney Safety Institute of America, the National Fireplace Institute, the Alliance for Green Heat and Lakes Region Community College Energy Program. We think its a major oversight that solid fuel appliances are not included in the SWS. They are a very popular appliance in many rural areas and its essential that there are standards for them. |  | Accepted | The committee agrees with the addition of a new specification. Please see draft of new specification to comment directly on the proposed specification.
7.0105.2 | Single Family Site-Built Housing, Manufactured Housing, Multifamily Housing | Baseload |  |  |  | Clothes Dryer | Safely reduce energy use for drying clothes | [5 empty] | My dryer is venting in the house at this time which causes condensation on the windows and walls |  | Rejected | Not an actual comment, but is a request from a client for services.

## Previosuly Adjudicated Comments (hidden)
Classification | Housing Type | Section | Topic | Subtopic | Detail | Title | Existing specification | Objective language | Status | Submitted | Updated | Submitted By | Comment | Justification/substantiation | Cost increase | Committee Adjudication | Committee Rationale for Decision | Proposed Title | Proposed specification | Proposed Objective language
2.0100.1b | Single-Family Homes | Health and Safety | Safe Work Practices | Safe Work Practices | Global Worker Safety | Hand protection | Durable and wrist-protecting gloves will be worn that can withstand work activity | Minimize skin contact with contaminantsProtect hands from sharp objects | Adjudicated - Redline only | 2014-08-06 | 2014-08-06 | Ricardo Trevino | energy efficiency upgrades often involve changing light bulbs, which can be very hot. Gloves should provide protection from burns. In multi family dwellings, for example, an installer may have have many units install energy efficient lights, and does not have the luxury of waiting for the existing high heat bulbs to cool before removing. | For objective(s), add: Insulate hand from exposure to heat. | Will require insulated gloves when handling hot light bulbs | Accepted | Clarifies the objective; OSHA 19190.138(a) uses the term "hazards" for cuts, abrasions, chemical or thermal burns and harmful temperatures | No change | No change | Minimize skin contact with contaminants Protect hands from hazards
2.0100.1c | Single-Family Homes | Health and Safety | Safe Work Practices | Safe Work Practices | Global Worker Safety | Respiratory protection | If the risk of airborne contaminants cannot be prevented, proper respiratory protection will be provided and worn (e.g., N-95 or equivalent face mask)When applying low pressure 2-component spray polyurethane foam, air purifying masks with an organic vapor cartridge and P-100 particulate filter will be usedWhen applying high-pressure SPF SPF Spray polyurethane foam insulation, supplied air respirators (SARs) will be usedConsult MSDSs for respiratory protection requirements | Minimize exposure to airborne contaminants (e.g., insulation materials, mold spores, feces, bacteria, chemicals) | Adjudicated - Redline only | 2014-06-29 | 2014-06-29 | Deborah Downing | SPF - Will be used - Rim Joist |  |  | Rejected | No change is suggested; low and high pressure SPF are already addressed in this specification and objective. (Suggest to commenter to resubmit with more clarity for their comment, invite to comment on appropriate detail and specification) | No change | No change | No change
2.0111.4c | Single-Family Homes | Health and Safety | Safe Work Practices | Basements and Crawl Spaces | Negative Pressure Contamination Control | Pressure | A negative pressure will be maintained in the crawl space with reference to the house while work is being performed in the crawl space | Prevent contaminants from entering house | Adjudicated - Redline only | 2014-07-14 | 2014-07-14 | John Krigger | Does the fan remain after you install the GMB? Is the pressure maintained permanently? Where does the make-up air come from? | I don't understand the point of this standard. |  | Rejected | Existing spec is clear about whether fan remains with language "while work is being performed." Make up air can come from anywhere as long as pressure in crawl WRT home is negative. | No change | No change | No change
2.0111.5a | Manufactured Housing | Health and Safety | Safe Work Practices | Basements and Crawl Spaces | Prework Qualifications (Home Installation) | Installation deficiencies | Any installation deficiencies that may affect worker safety or integrity or installed measures will be repaired before starting work | Ensure site is safe and ready for upgrade | Adjudicated - Redline only | 2014-05-08 | 2014-05-08 | Rachel Romero | This entire detail should apply to single-family and multifamily housing SWS too. Reasoning: All housing types should have this investigation and recommendation. Copy detail to both SF and MF. |  |  | Rejected | This SWS addresses inspection/assessment of installation of manufactured homes Spec 2.0111.2 already addresses this concern for SF | No change | No change | No change
2.0111.5a | Manufactured Housing | Health and Safety | Safe Work Practices | Basements and Crawl Spaces | Prework Qualifications (Home Installation) | Installation deficiencies | Any installation deficiencies that may affect worker safety or integrity or installed measures will be repaired before starting work | Ensure site is safe and ready for upgrade | Adjudicated - Redline only | 2014-07-14 | 2014-07-14 | John Krigger | Is the statement above what you mean. | Any foundation support problems will be repaired before beginning weatherization work. |  | Rejected | This SWS addresses site conditions prior to any weatherization measures and not solely foundation support | No change | No change | No change
2.0201.1a | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Assessment |  |  | Adjudicated - Redline only | 2014-04-21 | 2014-04-21 | Ted Williams | Minimum requirements from the National Fuel Gas Code (NFGC) Chapter 9, and their extraction into the International Fuel Gas Code (IFGC) and IRC Chapter G24 should be the primary means of addressing the second paragraph and should be so cited. Contrary to previous rejections of comments concerning references to the NFGC coverage, citations of IRC provisions would present the same issues (i.e., applicability to new construction and retrofits requiring code official intervention). More importantly, Section 9.1.24 of the NFGC (2015), which is approved by the ANSI Committee, would apply Chapter 9 to agent work implementing the SWS. Agents implementing the SWS without regard to minimum code would be in violation with this requirement. The serving utility should reexamine providing service to such occupancies. | n/a |  | Accepted with modification | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): This paragraph has been deleted in deference to spillage testing in new detail 2.0201.4a
2.0201.1e | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test |  |  | Adjudicated - Redline only | 2013-04-01 | 2013-04-01 | Thom Knoll | At 2.0201.1e, Depressurization Test, there appears to be magic with -3 pa which does not seem consistent with other standards of similar extraction. The BPI BA standard lists -3 pa limit only for a natural draft appliance commonly vented with a water heater. A whole table of values exist, including a lower threshold for orphaned water heater. | n/a |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Based on the new BPI 1200, the limit has been deleted
2.0201.1e | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test |  |  | Adjudicated - Redline only | 2014-03-28 | 2014-03-28 | DAVID CURTICE | Is this depressurization number for a declared appliance? More information is needed | n/a |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Based on the new BPI 1200, the limit has been deleted
2.0201.1e | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test |  |  | Adjudicated - Redline only | 2014-04-14 | 2014-04-14 | Brad Turner | This specification seems to potentially conflict with the more detailed specifications listed under Section 2.0299.1 - Combustion Appliance Depressurization Tables. 2.0299.1 lists various manufacturer's certified negative pressure tolerance ratings, most of which are more negative than the -3 Pa. limit listed in 2.0201.1e. Suggest language such as, "...and will not be more negative than manufacturer's certified negative pressure tolerance ratings listed in 2.0299.1 depending on appliance type and/or configuration in combustion appliance zone." NOTE - BPI HEP Certification exams (Quality Control Inspector, Energy Auditor, Crew Leader) do require candidates to perform Worst Case CAZ Depressurization tests but DO NOT establish any limits/recommendations based on the appliance type/configuration. Candidate is only required to place CAZ in proper Worst Case scenario and carry out remaining CAZ tests under those conditions. This is confusing for trainers/candidates when the exams are supposed to be based on the SWS. | n/a |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Based on the new BPI 1200, the limit has been deleted
2.0201.1e | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test |  |  | Adjudicated - Redline only | 2014-04-21 | 2014-04-21 | Thom Knoll | Prior comment redirect should be 2.0299.1a | n/a |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance):
2.0201.1e | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test |  |  | Adjudicated - Redline only | 2014-04-21 | 2014-04-21 | Gene Elwood | The -3 pascals is in conflict with depressurization limits in 2.0299.1. | n/a |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): All limits have been deleted
2.0201.1e | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test |  |  | Adjudicated - Redline only | 2014-04-21 | 2014-04-21 | Thom Knoll | While this specification lists only -3 pa, at 2.0199.1a is a list of equipment types with differing depressurization limits. Where does the -3 value come from? | n/a |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Detail 2.0299 has been deleted; -3 value deleted
2.0201.1e | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test |  |  | Adjudicated - Redline only | 2014-05-14 | 2014-05-14 | Darrel Tenter Tenter | The limit of -3 pa conflicts with 2.0299.1 Combustion Appliance Depressurization Limits Table, which shows many CAZ depressurization limits depending on equipment. Suggested change to this language: Depressurization test will include exhaust fans, interior door closure, or duct leakage, or a combination thereof, and will not be more negative than the limits contained in 2.0299.1 Combustion Appliance Depressurization Limits Table. |  |  | Accepted with modification | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): All limits have been deleted
2.0201.1e | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test |  |  | Adjudicated - Redline only | 2014-10-20 | 2014-10-20 | Steve Divan | By limiting the depressurization of any combustion zone to -3 pa is in conflict with 2.0299.1a-i. The depressurization limit ranges from -2 to -25 in those sections. Section 2.0201.1e should be changed to allow for differences between appliances detailed in 2.0299.1a-i. | "Depressurization test will include exhaust fans, interior door closure, or duct leakage, or a combination thereof, and will not be more negative than the Manufacturer's certified negative pressure tolerance rating limit when accounting for base pressure" |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): All limits have been deleted
2.0201.1e | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test |  |  | Adjudicated - Redline only | 2014-10-31 | 2014-10-31 | Colorado Energy... | I am confused as what to follow. It states -3 pascals max for depressurization test however 2.0299.1A-I lists depressurization limits for specific appliances. These two specifications appear to be contradictory. | I am confused as what to follow. It states -3 pascals max for depressurization test however 2.0299.1A-I lists depressurization limits for specific appliances. These two specifications appear to be contradictory. |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): All limits have been deleted
2.0201.1e | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test |  |  | Adjudicated - Redline only | 2015-03-30 | 2015-03-30 | Charles Kurnik | Need clarification. | What if it is "more negative"? Should an exhaust fan be turned off? |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): BPI 1200 method now specified
2.0201.1f | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Spillage test |  |  | Adjudicated - Redline only | 2014-04-14 | 2014-04-14 | Brad Turner | BPI HEP Certification Field Exams (Quality Control Inspector, Energy Auditor, Crew Leader) require candidates to identify time limits for spillage, perform spillage tests, and determine if the appliance passes the spillage tests BASED ON BPI STANDARDS (BPI 1200), which are different that the spillage time limits in SWS. Recommend aligning SWS + BPI 1200 + and BPI HEP Field Exam requirements and time limits. | n/a |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Aligned with BPI 1200 and NFGC; moved to new specification 2.0201.4a
2.0201.1f | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Spillage test |  |  | Adjudicated - Redline only | 2014-04-23 | 2014-04-23 | Darrel Tenter Tenter | Gasses as used here is misspelled. The plural form of gas is gases. Gasses is the present tense verb. As in "Foam insulation out-gasses". |  |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance):
2.0201.1f | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Spillage test |  |  | Adjudicated - Redline only | 2014-08-08 | 2014-08-08 | Roger Smith | BPI standards | This standard suggests two minutes for spillage, whereas BPI says one minute. Which is correct? | no | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): This item deleted in favor of new specification--2.0201.4a--which has the spillage requirements
2.0201.1g | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Carbon monoxide ( CO CO Carbon monoxide ) test in appliance vent |  |  | Adjudicated - Redline only | 2014-04-14 | 2014-04-14 | Brad Turner | BPI HEP Certification Field Exams (Quality Control Inspector, Energy Auditor, Crew Leader) require candidates to measure combustion appliance CO and interpret results BASED ON BPI STANDARDS (BPI 1200), which in some cases are different that the CO thresholds in SWS. BPI Standard 1200 references "ANSI/BSR Z223.1/NFPA 54, National Fuel Gas Code, Table G.6: CO Thresholds", siting CO threshold limits which are different from those listed here in SWS. Recommend aligning SWS + BPI 1200 + and BPI HEP Field Exam requirements and threshold limits. | n/a |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Aligned with BPI 1200 and NFGC; moved to new specification 2.0201.4b
2.0201.1i | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Combustion safety testing at completion of retrofitting home |  |  | Adjudicated - Redline only | 2015-01-07 | 2015-01-07 | Steve Divan | We recognize the importance of doing a daily test out when a potential hazardous situation exists, but this should only be required when a trained professional identifies a problem. The vast majority of homes do not require testing on this level. To add an additional level of safety, most programs require a CO alarm be installed in every home at the time of the audit and a final test out at the conclusion of the job. Additionally, 2.0201.1i is in conflict with 2.0201.3h which is the manufactured home CAZ testing requirements. 2.0201.3h simply states that a final combustion test must be completed at project completion. This seems to be a more reasonable and appropriate standard for single family homes also. Any standard should consider whether the appliance is sealed combustion, direct vent or even fan assisted, reasonably consider the level of air sealing performed and consider the original tightness of the building. A blanket requirement to test at the end of each work day regardless of conditions and equipment type is costly and unnecessary. | Final combustion testing will be conducted at project completion to ensure compliance with the above specifications | No, The current SWS will cause costs to rise.The costs associated with training contractors, purchasing the required equipment and paying for contractor or agency staff time to perform these tests would be an unnecessary burden on the WAP program. The potential costs of performing daily testing are significant and have not been shown to be necessary. | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Many programs do NOT install a CO alarm at audit; the importance of combustion safety makes testing at the end of each day important for the overnight safety of the residents
2.0201.2a | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Safety | Outside combustion make-up air |  |  | Adjudicated - Redline only | 2014-05-15 | 2014-05-15 | John Krigger | This detail says combustion testing. Is this the place for this standard? Do you mean to require outdoor combustion air duct for every tuned-up appliance? Every replaced appliance? I disagree that this is necessary. It is expensive and has possible unintended consequences. |  |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): The word "Testing" removed from specification, title now indicates make-up air
2.0201.2a | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Safety | Outside combustion make-up air |  |  | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | I think that this is what the standard means. If not, what does it mean? | For condensing furnaces, install dedicated combustion air pipe directly to the appliance. |  | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): This could also be for other appliances. This is make-up air, not direct-vent air
2.0201.2b | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Safety | New appliances |  |  | Adjudicated - Redline only | 2014-05-15 | 2014-05-15 | John Krigger | The second paragraph needs to be more specific. |  |  | Accepted with modification | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Added clarifying sentence
2.0201.2b | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Safety | New appliances |  |  | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | I've got the code open and have no idea what this standard is saying. The IRC reference is about clearance. What is this standard requiring? | Too vague. Delete |  | Accepted with modification | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Reference to specific section deleted
2.0201.2d | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Safety | Gas ovens |  |  | Adjudicated - Redline only | 2014-04-14 | 2014-04-14 | Brad Turner | BPI HEP Certification Field Exams (Quality Control Inspector, Energy Auditor, Crew Leader) require candidates to measure oven CO and interpret results BASED ON BPI STANDARDS (BPI 1200), which are different than the threshold limits in SWS. BPI Standard 1200 references "ANSI/BSR Z223.1/NFPA 54, National Fuel Gas Code, Table G.6: CO Thresholds", siting an oven CO threshold limit of 225 ppm As Measured, which is different from those thresholds listed here in SWS. Recommend aligning SWS + BPI 1200 + and BPI HEP Field Exam requirements and threshold limits. | n/a |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): 225 as-measured now used
2.0201.2d | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Safety | Gas ovens |  |  | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | I'm getting questions about how 200 lines up with 800 in this case when it lines up with 400 in other sections. | 200/400??? |  | Accepted with modification | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): The requirement has been aligned with BPI 1200 and the NFGC at 225 ppm as-measured
2.0201.3c | Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Venting |  |  | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | Mobile homes built since the early to mid seventies have been required to have sealed combustion, meaning that they have no draft regulator. Slope isn't an issue for mobile home furnaces, which vent straight up. | Verify the presence of a sealed-combustion venting system. Verify that the furnace's chimney and combustion-air delivery are properly connected and aren't damaged. |  | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): This section can apply to older manufactured homes
2.0201.3e | Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test |  |  | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | CAZ testing is required for open combustion appliances and isn't required for sealed combustion appliances. | When a mobile home furnace is operating, the mobile home must have no open combustion heating devices because of the strong negative pressure created by the furnace. |  | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): This section is not about only furnaces or sealed combustion
2.0201.3e | Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test |  |  | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | Site-built spec applied to mobile home as duplicated in 5.3003 | Change to open combustion from natural draft. |  | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Language is considered appropriate
2.0201.3e | Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test |  |  | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | Site-built spec applied to mobile home as duplicated in 5.3003 | Change to open combustion from natural draft. |  | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Language is considered appropriate
2.0201.3e | Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test |  |  | Adjudicated - Redline only | 2015-03-30 | 2015-03-30 | Charles Kurnik | When dealing with combustion byproducts, it seems like the guidance should be consistent. | Most parallel details in the Manufactured Housing version (2.0201.3) do not match the single family version (2.0201.1). It seems like they should. |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Single-family and manufactured housing details are now aligned
2.0201.3f | Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Spillage test |  |  | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | Again the sealed combustion mobile home appliance shouldn't spill. | No detectable spillage allowed. |  | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): This section is not only about furnaces or sealed combustion
2.0201.3f | Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Spillage test |  |  | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | If you have an operable furnace and an open-combustion appliance in a mobile, that is unsafe and should be mitigated. Substitute open-combustion for natural draft -- natural draft isn't the problem. | A mobile home furnace should have no detectable spillage because it is sealed combustion. If a mobile home has an open combustion furnace, the home should have both supply and return ducts. |  | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): There are many manufactured homes with natural draft appliances, including water heaters; his section is not just about furnaces, nor about sealed combustion
2.0201.3f | Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Spillage test |  |  | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | Spillage at anything but a very small level is unacceptable in a sealed-combustion appliance. Same problems as 5.3003 | 100/200 dilemma. |  | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): This section is not about sealed combustion equipment
2.0201.3g | Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Carbon monoxide ( CO CO Carbon monoxide ) test in appliance vent |  |  | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | Here is another 100 ppm number that makes no sense in light of the new 200 ppm initiative. This is sealed combustion equipment after all. | 200/400 if you decide to stick with that standard. |  | Accepted with modification | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): This section is not only about furnaces, or about sealed combustion; however, the CO limits have been updated
2.0201.3g | Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Carbon monoxide ( CO CO Carbon monoxide ) test in appliance vent |  |  | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | How do you justify having a higher bar for sealed combustion appliances in mobile homes? | 100/200 dilemma. |  | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): This section is not about sealed combustion equipment
2.0201.3g | Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Carbon monoxide ( CO CO Carbon monoxide ) test in appliance vent |  |  | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | Why more stringent for sealed combustion furnaces? | 100/200 dilemma |  | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): This section is not only about furnaces or sealed combustion
2.0203.1a | Single-Family Homes | Health and Safety | Combustion Safety | Vented Gas Appliances | Combustion Air for Natural Draft Appliances | Required combustion air |  |  | Adjudicated - Redline only | 2014-12-18 | 2014-12-18 | John Krigger | I think that many agencies interpret this standard as a requirement to install supplemental combustion air, which is usually unnecessary. I have a section in our field guides outlining a procedure to evaluate combustion air with a combustion analyzer. | During worst-case testing, use a combustion analyzer to measure both CO and oxygen (O2).The O2 is an indicator of excess combustion air, and CO may be an indicator of insufficient combustion air. |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Now specifies that combustion air only gets added when necessary to solve spillage issues
2.0203.2a | Single-Family Homes | Health and Safety | Combustion Safety | Vented Gas Appliances | Combustion Flue Gas&mdash;Orphaned Water Heaters | Spillage testing |  |  | Adjudicated - Redline only | 2014-04-21 | 2014-04-21 | Ted Williams | The two minute threshold is in conflict with the Z21.10.1 design certification standard for safety and is ad hoc. The threshold should be increased to 5 minutes generally or shorter time durations based on additional criteria (e.g., hot vent initial conditions). | n/a |  | Accepted with modification | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Two minutes is now only for appliances presumed to be in warm vent condition (furnaces in heating mode, water heaters); five minutes is specified for furnaces not in heating mode
2.0203.2a | Single-Family Homes | Health and Safety | Combustion Safety | Vented Gas Appliances | Combustion Flue Gas&mdash;Orphaned Water Heaters | Spillage testing |  |  | Adjudicated - Redline only | 2014-04-23 | 2014-04-23 | Darrel Tenter Tenter | Comment related to the desired outcome for this detail. Gasses as used here is misspelled. The plural form of gas is gases. Gasses is the present tense verb. As in "Foam insulation out-gasses". |  |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance):
2.0203.3a | Single-Family Homes | Health and Safety | Combustion Safety | Vented Gas Appliances | Draft Regulation&mdash;Category I Appliance | Assessment |  |  | Adjudicated - Redline only | 2014-04-23 | 2014-04-23 | Darrel Tenter Tenter | Comment related to the desired outcome for this detail. Gasses as used here is misspelled. The plural form of gas is gases. Gasses is the present tense verb. As in "Foam insulation out-gasses". |  |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance):
2.0203.3c | Single-Family Homes | Health and Safety | Combustion Safety | Vented Gas Appliances | Draft Regulation&mdash;Category I Appliance | Retesting spillage |  |  | Adjudicated - Redline only | 2015-12-15 | 2015-12-15 | Kelly Cutchin C... | Align with BPI 1200 | Where is the first mention of testing spillage in this detail? If this is retesting, the vent will already be warm so the 2 minute limited works. Should there be a row added above that mentions spillage testing with the 2 warm/5 cold vent time limits? |  | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Detail was deleted because draft regulators only apply for oil-fired appliances and don't belong in the gas-fired section
2.0203.4c | Manufactured Housing | Health and Safety | Combustion Safety | Vented Gas Appliances | Combustion Air for Natural Draft Appliances | Spillage testing |  |  | Adjudicated - Redline only | 2015-12-15 | 2015-12-15 | Kelly Cutchin C... | Align with BPI 1200 | Spec: If spillage in a combustion appliance with a warm vent exceeds two minutes during pressure testing, specify measures to mitigate. If spillage in a combustion appliance with a cold vent exceeds five minutes during pressure testing, specify measures to mitigate. Objective: Detect excessive spillage of combustion gases. |  | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Detail combined with Detail 2.0203.1; Spec 2.0203.1c was added to include new testing language
2.0203.5a | Manufactured Housing | Health and Safety | Combustion Safety | Vented Gas Appliances | Combustion Flue Gas&#173;&mdash;Orphaned Water Heaters | Spillage testing |  |  | Adjudicated - Redline only | 2015-12-15 | 2015-12-15 | Kelly Cutchin C... | Align with BPI 1200 | Spec: If spillage in a combustion appliance with a warm vent exceeds two minutes during pressure testing, specify measures to mitigate. If spillage in a combustion appliance with a cold vent exceeds five minutes during pressure testing, specify measures to mitigate. Objective: Detect excessive spillage of combustion gases. |  | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Detail was combined with 2.0203.2; Spec 2.0203.2a was modified to include new language
2.0203.5b | Manufactured Housing | Health and Safety | Combustion Safety | Vented Gas Appliances | Combustion Flue Gas&#173;&mdash;Orphaned Water Heaters | Retesting spillage |  |  | Adjudicated - Redline only | 2015-12-15 | 2015-12-15 | Kelly Cutchin C... | Clarify | Objective: Ensure appliance is not spilling longer than 2 minutes with a warm vent. |  | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Detail was combined with 2.0203.2; Spec 2.0203.2c was modified to include new language
2.0203.6c | Manufactured Housing | Health and Safety | Combustion Safety | Vented Gas Appliances | Draft Regulation&mdash;Category I Appliance | Retesting spillage |  |  | Adjudicated - Redline only | 2015-12-15 | 2015-12-15 | Kelly Cutchin C... | Clarify language. | This is about retesting, but is testing for the first time mentioned in this detail? Consider adding a row above this one. Then clarify objective here: Ensure appliance is not spilling longer than 2 minutes with a warm vent. |  | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Detail was deleted because draft regulators only apply for oil-fired appliances and don't belong in the gas-fired section
2.0299.1a | Single-Family Homes | Health and Safety | Combustion Safety | Additional Resources | Combustion Appliance Depressurization Limits Table | Atmospheric water heater only (Category I, natural draft), open-combustion appliances |  |  | Adjudicated - Redline only | 2014-04-21 | 2014-04-21 | Frank Stanonik | Delete this entire section. There is no recognized test procedure to measure the depressurization resistance of gas and oil-fired appliances so there is no such thing as certified negative pressure tolerance rating. If energy upgrades in an existing home lead to a depressurization issue then the preferred action is not to try to fix the newly created problem but rather to not do the upgrades that created the problem. | n/a |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance):
2.0401.1b | Single-Family Homes | Health and Safety | Moisture | Air Sealing | Air Sealing Moisture Precautions | Moisture precautions for crawl spaces | Exposed earth will be covered with a continuous, durable, sealed Class 1 vapor retarder Vapor retarder A material that slows the passage of water vapor and contains a perm rating above 1 a minimum of 6 mils in thickness Plastic, foil or any other Class 1 vapor barrier Vapor barrier A material that retards the passage of water vapor and contains a perm rating of less than 1 /retarder will not be used in hot-humid climatesAll accessible penetrations between the crawl space or basement and outside will be sealedHoles between the crawl space or basement and the living space will be sealed | Ensure durability of repairsReduce potential for occupant exposure to mold and other moisture-related hazards | Adjudicated - Redline only | 2014-12-09 | 2014-12-09 | Kelly Cutchin C... | As currently written, the spec indicates you would not install ground cover in hot humid climates, but I don't think that's what the authors intended. I think we still want to cover exposed earth in crawls and basements, but want to avoid trapping moisture against potentially cooler-than-outdoor building components. | Revise 2nd paragraph of spec to: Plastic, foil or any other Class 1 vapor barrier/retarder will not be installed in a way that could trap moisture against building materials in hot-humid climates | No. | Accepted with modification | Clarifies the intent of the SWS and removed uneeded langauge related to basements | No change | Exposed earth will be covered with a continuous, durable, sealed Class 1 vapor retarder a minimum of 6 mils in thickness Any vapor retarder shall not encapsulate wood building materials or spray foam Holes between the crawl space and the living space will be sealed | No change
2.0403.1d | Single-Family Homes | Health and Safety | Moisture | Vapor Barriers | Vented Crawl Spaces&mdash;Ground Moisture Barrier | Overlap seams | When seams exist, they will be overlapped a minimum of 12" using reverse or upslope lapping technique Reverse or upslope lapping technique Upper course laps under a lower course to keep the moisture under the barrier | Keep water under the linerReduce the likelihood of damage at seams | Adjudicated - Redline only | 2015-04-15 | 2015-04-15 | John Krigger | If the goal is to exclude water, water vapor, and air from the ground, the seams should be sealed. | When seams exist, they will be overlapped a minimum of 12" using reverse or upslope lapping technique. Seams must be sealed with tape or sealant. |  | Rejected | Current SWS is able to achieve its objective without sealing the seams | No change | No change | No change
2.0403.1e | Single-Family Homes | Health and Safety | Moisture | Vapor Barriers | Vented Crawl Spaces&mdash;Ground Moisture Barrier | Fastening | Ground moisture barrier will be fastened to ground with durable fasteners or ballast(s) and extend a minimum of 6" up the foundation wall | Prevent movement of the ground moisture barrier | Adjudicated - Redline only | 2014-12-05 | 2014-12-05 | John Davies | Fastening up the wall in existing construction is an added cost burden for a weatherization program, generally not necessary and overkill in the dryer areas of the country. | Fastening required when ground moisture barrier is to be installed on sloping ground, high traffic area or when cover will be exposed to wind. | The proposed change allows fastening but does not require it | Accepted | Addresses specifc situation of the SWS. Still meets objective while reducing cost of measure. | No change | When ground moisture barrier is installed on sloping ground, may be exposed to wind, or accessed for routine maintenance or storage it will be fastened to ground with durable fasteners or ballast(s) | No change
2.0403.2e | Single-Family Homes | Health and Safety | Moisture | Vapor Barriers | Closed Crawl Spaces&mdash;Ground Moisture Barriers | Fastening | The air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary and ground moisture barrier will be fastened to the ground to prevent movement in accordance with ASTM ASTM ASTM International, www.astm.org E1643 and manufacturer's recommendations | Prevent movement and uplift of the air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary and ground moisture barrier | Adjudicated - Redline only | 2015-05-29 | 2015-05-29 | Kelly Cutchin C... | Since this detail addresses closed crawl spaces, it is unlikely that wind will cause uplift of the moisture barrier. Suggest rephrasing so only in situations where the space will be disturbed requires the fastening. | In situations where the crawl space is accessed for routine maintenance or storage, the air barrier and ground moisture barrier will be fastened to the ground to prevent movement in accordance with ASTM E1643 and manufacturer's recommendations | No, reduce it. | Accepted with modification | Addresses specifc situation of the SWS. Still meets objective while reducing cost of measure | No change | When ground moisture barrier is installed on sloping ground, or accessed for routine maintenance or storage it will be fastened to ground with durable fasteners or ballast(s) | No change
2.0403.3b | Single-Family Homes | Health and Safety | Moisture | Vapor Barriers | Closed Crawl Spaces&mdash;Vapor Retarders on Walls | Coverage | An air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary and vapor retarder Vapor retarder A material that slows the passage of water vapor and contains a perm rating above 1 will be installed a minimum of 1' or as high as possible above outside grade | Prevent air and moisture penetration | Adjudicated - Redline only | 2014-03-31 | 2014-07-14 | John Krigger | This spec varies from the IRC, which says take the vapor barrier 6 inches up the wall. I think it is bad practice to install a vapor barrier on the inside of a crawl space wall, higher than 6 inches. The vapor barrier reduces drying potential and could harbor pests. What about the ventilation that the IRC requires? I don't think that is always necessary, but the IRC says you need 1/1500 of natural or an exhaust fan connect to the living space or a supply register in the crawl space of a home that doesn't have AC. The "doesn't have AC" is my spec responding to an oversight in the code and in common building practice. | n/a |  | Rejected | Data from www.crawlspaces.org demonstrates that it is not a bad practice; please resubmit your comment if it was misinterpreted by the committee | No change | No change | No change
2.0403.3b | Single-Family Homes | Health and Safety | Moisture | Vapor Barriers | Closed Crawl Spaces&mdash;Vapor Retarders on Walls | Coverage | An air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary and vapor retarder Vapor retarder A material that slows the passage of water vapor and contains a perm rating above 1 will be installed a minimum of 1' or as high as possible above outside grade | Prevent air and moisture penetration | Adjudicated - Redline only | 2014-04-17 | 2014-07-14 | John Krigger | I really don't like the idea of installing vapor barriers on the interior of foundation walls. It is wishful thinking that the vapor barrier will mitigate moisture problems if the exterior wall isn't waterproofed or dampproofed. I think that the 6-inch ground moisture barrier overlap onto the wall is good practice but that running the vapor barrier further up the wall is pointless and could be counterproductive. | n/a |  | Rejected | Data from www.crawlspaces.org demonstrates that it is not a bad practice; please resubmit your comment if it was misinterpreted by the committee | No change | No change | No change
2.0601.1b | Single-Family Homes | Health and Safety | Electrical | Knob and Tube Wiring | Knob and Tube Wiring | Live wire testing | Non-contact testing method will be used to determine if wiring is live | Protect occupant safetyPreserve the integrity and safety of the house | Adjudicated - Redline only | 2014-05-02 | 2014-05-02 | Rachel Romero | Per executive committee, change to "Appropriate testing method will be used to determine if wiring is live by the authority having jurisdiction" Rationale: Non-contact testing was a vague term. |  |  | Rejected | The SWS intends that testing should be conducted without contacting the wire and therefore the language is sufficient | No change | No change | No change
2.0601.1c | Single-Family Homes | Health and Safety | Electrical | Knob and Tube Wiring | Knob and Tube Wiring | Isolation and protection | Live knob and tube will not be covered or surrounded; required by the National Electrical Code ( NEC NEC National Electrical Code ) or authority having jurisdiction A licensed electrical contractor will inspect and certify wiring to be safe and place a warning at all entries to the attic about the presence of knob and tube wiringA dam that does not cover the top will be created to separate insulation from the wire path | Ensure occupant safety Preserve the integrity and safety of the house | Adjudicated - Redline only | 2014-05-02 | 2014-05-02 | Rachel Romero | Per Executive Committee, replace with "Proper clearance will be maintained around live knob and tube; required by the National Electrical Code ( NEC ) or authority having jurisdiction A dam that does not cover the top will be created to separate insulation from the wire path" | Rationale: Defer to the authority having jurisdiction for the inspection requirements. |  | Accepted with modification | Agree with rationale of commenter | No change | Proper clearance will be maintained around live knob and tube as required by the National Electrical Code ( NEC ) or authority having jurisdiction When required, a dam that does not cover the top will be created to separate insulation from the wire path | No change
2.0702.1b | Single-Family Homes | Health and Safety | Occupant Education and Access | Installed Equipment | Warranty and Service Agreement | Warranty renewal and service agreement | An option for annual inspection and renewal of warranty and service agreement for up to 10 years will be offered at a cost (requirement for installers) | Provide occupants with an option for extending the warranty and service agreement | Adjudicated - Redline only | 2014-12-02 | 2014-12-02 | Shawn Turi | I am a contractor not the manufacturer nor am I an underwriter for an Insurance Company. I do not understand how I would be responsible for offering a 10 year replacement warranty for equipment that I only installed but did not build. If the manufacturer does not offer extended parts and labor for their appliances, how then can you make a small, independent businessman be responsible for what the manfacturer should be offering? I will be consulting my lawyer about these concerns. | I feel that the warranty on installed appliances should be for only what the manufactured warranties are. For instance, water heaters have 6 year tank and parts, and furnaces have 10 year parts and limited life time heat exchangers if registerd online within 90 days by the costumer. Ashrae fans usually have a 1 year to 2 year warranty.I propose that the customer be made aware of the manufacturer warranties and not a 10 year replacement and labor warranty. I do agree that I should offer a one year warranty on any materials used and craftmanship of the labor. |  | Accepted | We cannot force installers to offer longer warranties than manufacturers. Suggest following modifications to distiguish between company warranty and manufacturer warranty. | Warranty and Maintenance Agreement - Client Education | Provide occupants with manufacturers' warranties on installed equipment and inform of installer maintenance agreement options Share information on company related annual inspections and maintenance agreements as well as manufacturer related warranty details | Ensure occupants are aware of warranty and maintenance agreement options
3.1001.1a | Single-Family Homes | Air Sealing | Attics | Penetrations and Chases | Penetrations and Chases | Pre-inspection | An inspection will be conducted for mold, water leaks, and water damage before sealing a chaseRepairs will be completed before work | Repair moisture-related issues | Adjudicated - Redline only | 2015-04-15 | 2015-04-15 | Charles Kurnik | This is a test of justification | This is a test of new text |  | Rejected | Test of system, not comment on SWS. | No change | No change | No change
3.1001.4a | Manufactured Housing | Air Sealing | Attics | Penetrations and Chases | General Penetrations (Electrical, HVAC, Plumbing, Vent Termination, Recessed Lighting) | Work assessment | Installer prework assessment will be conducted to determine: Structural integrity Roof leaks Insect infestation Accessibility Number, type, size, and location of penetrations | Ensure work space is safe and ready for air sealingVerify scope of work | Adjudicated - Redline only | 2014-06-29 | 2014-06-29 | Deborah Downing | Testing Template Comments |  |  | Rejected | Test of system, not comment on SWS. | No change | No change | No change
3.1003.1a | Single-Family Homes | Air Sealing | Attics | Dropped Ceilings and Soffits | New Ceiling Below Original&mdash;Old Ceiling Intact or Repairable | Pre-inspection | An inspection will be conducted for mold, water leaks, and water damage before sealing a dropped ceiling or soffitRepairs will be completed before work begins | Repair moisture-related issues | Adjudicated - Redline only | 2014-05-18 | 2014-05-18 | Jeffrey Granger | This is an area for you to enter comments. |  |  | Rejected | Test of system, not comment on SWS. | No change | No change | No change
3.1201.1e | Single-Family Homes | Air Sealing | Windows and Doors | Maintenance, Repair, and Sealing | Double-Hung Wood Windows | Sash replacement | Lower sash will have the same bevel on the bottom rail as the sillSash will be water-sealed and primed | Ensure sash remains in a fixed position when open or partially openMaintain operability of the window | Adjudicated - Redline only | 2015-01-05 | 2015-01-05 | Peter Newton | The bevel of the lower sash should match the bevel of the sill in order to provide a complete seal when closed as well as prevent water infiltration beneath sash. | Form a complete seal from the bottom of the lower sash to the sill. |  | Accepted | Clarifies SWS and achieves stated objective. | No change | No change | Ensure sash remains in a fixed position when open or partially open Maintain operability of the window Form a complete seal from the bottom of the lower sash to the sill
3.1203.1b | Single-Family Homes | Air Sealing | Windows and Doors | Replacement | Replacement Window in Existing Window Frame | Opening preparation | Interior stops, sashes, parting strips, and pulleys will be removedOpening will be cleaned | Provide a clean opening for replacement window unit | Adjudicated - Redline only | 2014-05-09 | 2014-05-09 | Pete Hans | wash windows with cool-aid and paint glass |  |  | Rejected | No justification/substantiation provided. | No change | No change | No change
3.1402.2a | Single-Family Homes | Air Sealing | Basements and Crawl Spaces | Crawl Spaces | Closed Crawl Spaces&mdash;Air Sealing Foundation Vents | Vent closure | Vent opening will be permanently closed and sealed | Prevent air and moisture penetration | Adjudicated - Redline only | 2014-05-14 | 2014-05-14 | Darrel Tenter Tenter | In certain circumstances we should not be permanently sealing off the CS vents. How does this specification not conflict with other specs that define when the CS vents should be sealed, and what must be done first. 2.0404.2 for example. Either delete this specification, or add some a decision points to decide if the CS vents should be sealed or not. |  |  | Rejected | The SWS is not a prescriptive tool for every situation | No change | No change | No change
3.1501.1a | Single-Family Homes | Air Sealing | Attached Garages | Garage Openings | Penetrations, Cracks, and Doors Between Garage and House | Penetrations | All lighting fixtures, wiring, plumbing, venting, ducting, and gas piping penetrations will be sealed | Prevent air leakage and pollutant entry | Adjudicated - Redline only | 2014-09-22 | 2014-09-22 | Nicole Harrison | Reason for edit | Edit |  | Rejected | Test of system, not comment on SWS. | No change | No change | No change
3.1601.8c | Multifamily Homes | Air Sealing | Ducts | Duct Preparation | Preparation and Mechanical Fastening&mdash;Mid and High Rise | Flex to metal (150) | Joints will be fastened with tie bands using a tie band Tie band A strap, often made of nylon, that mechanically squeezes a flexible duct to a fitting. Must have a minimum performance temperature rating of 165° (per UL 181A-type test) and a minimum tensile strength rating of 50 pounds tensioning tool or mechanical band, and sealed with approved mastic and UL181B tape | Ensure joints are durable Reduce air leakage | Adjudicated - Redline only | 2014-12-03 | 2014-12-03 | Jim Harmon Harmon | The joint needs to be (1) secure and (2) sealed. The tie band or mechanical band secures the joint, and the mastic OR tape will seal the joint. Therefore both mastic AND tape would be redundant and a waste of resources. See research by Bruce Manclark. | Joints will be fastened with tie bands using a tie band tensioning tool or mechanical band, and sealed with approved mastic OR UL181B tape |  | Accepted | Clarifies expectations of measure | No change | Joints will be fastened with tie bands using a tie band tensioning tool or mechanical band, and sealed with approved mastic OR UL181B tape. Must have a minimum performance temperature rating of 165° (per UL 181A-type test) and a minimum tensile strength rating of 50 pounds tensioning tool or mechanical band, and sealed with approved mastic and UL181B tape | No change
3.1802.1a | Multifamily Homes | Air Sealing | Roofs | Roof/Wall Connections | Roof/Exterior Wall Connection, Including Joints at Roof/Parapet/Wall Connections | Pre-inspection | Conduct pre-inspection in accordance with SWS 2.0100.4 Work Area Inspection and StabilizationExisting water control measures will be identifiedAir sealing locations will be identified between the roof and the exterior wall | Provide a safe and stable work environmentAvoid compromising existing water control systemEnsure a continuous air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary will be appropriately located at the roof/exterior wall junction | Adjudicated - Redline only | 2014-12-08 | 2014-12-08 | Kelly Cutchin C... | Parapet walls sometimes exist in SF homes, and nothing from this detail would preclude its inclusion in the SF SWS (and hence provide reference for field guides, etc.) | No new text - suggest adding this to Single Family Library (entire detail, not just this row). | No. | Accepted | (No language change. Add detail to SF.) | No change | No change | No change
4.1001.1b | Single-Family Homes | Insulation | Attics | General Preparation | Non-Insulation Contact (IC) Recessed Light | Enclosure top | The top-fire rated enclosure material will have an R-value of 0.5 or lessThe top of the enclosure will be left free of insulation | Prevent heat build up | Adjudicated - Redline only | 2014-11-03 | 2014-11-03 | Steve Divan | 5/8" Sheetrock has an R-value of .56. 4.1001.1a indicates that 5/8" Sheetrock is an acceptable material. The R-value should be changed to avoid any conflict between the two sections. | The top-fire rated enclosure material will have an R-value of 0.56 or less. |  | Accepted | Clarifies SWS and achieves stated objective. | No change | The top-fire rated enclosure material will have an R-value of 0.56 or less The top of the enclosure will be left free of insulation | No change
4.1001.3b | Single-Family Homes | Insulation | Attics | General Preparation | Fireplace Chimney and Combustion Flue Vents | Required clearance | A rigid dam having a height greater than the insulation to be installed will be constructed to ensure a 3" clearance between combustion flue vent and dam Chimney vents will have an airspace clearance to combustibles in accordance with 2012 IRC IRC International Residential Code M1801.3.4 | Ensure dam material does not bend, move, or sagPrevent a fire hazard | Adjudicated - Redline only | 2015-01-26 | 2015-01-26 | John Krigger | Why create a larger area of insulation void than necessary. L-vent is 3, B-vent: 2; masonry interior: 2; masonry exterior: 1 and all fuel:2. These are NFPA figures and plenty conservative. Why require 3"? The IRC section referenced says nothing important. | A rigid dam having a height greater than the insulation to be installed will be constructed to ensure a 3" clearance between combustion flue vent and combustible materials, unless the flue vent is listed for a lesser clearance. |  | Accepted | Clarifies SWS and achieves stated objective. | No change | A rigid dam having a height to ensure a 3" clearance area free of insulation or combustibles between combustion flue vent and dam, unless the flue vent is listed for a lesser clearance | No change
4.1001.3b | Single-Family Homes | Insulation | Attics | General Preparation | Fireplace Chimney and Combustion Flue Vents | Required clearance | A rigid dam having a height greater than the insulation to be installed will be constructed to ensure a 3" clearance between combustion flue vent and dam Chimney vents will have an airspace clearance to combustibles in accordance with 2012 IRC IRC International Residential Code M1801.3.4 | Ensure dam material does not bend, move, or sagPrevent a fire hazard | Adjudicated - Redline only | 2015-04-24 | 2015-04-24 | Kelly Cutchin C... | Consider adding this entire detail to the Manufactured Housing library. Currently, I can't find anything about prepping for attic insulation in MH. | N/A - suggesting adding to MH library. | No. | Accepted | Clarifies SWS and achieves stated objective. | No change | A rigid dam having a height to ensure a 3" clearance area free of insulation or combustibles between combustion flue vent and dam, unless the flue vent is listed for a lesser clearance | No change
4.1002.2b | Single-Family Homes, Manufactured Housing | Insulation | Attics | Above Roof Deck Insulation | Above Deck Roof Deck Insulation: Installation | Installation | Insulation will be installed according to manufacturer specifications without gaps, voids, compressions, misalignments, or wind intrusionsInsulation will be installed to prescribed R-value | Install insulation properly | Adjudicated - Redline only | 2014-06-10 | 2014-06-10 | Rachel Romero | The language here refers to blow-in insulation. Only regisit insulation goes above the roof deck. |  |  | Rejected | Rigid insulation can be installed to allow gaps, voids, and wind intrusion. This SWS clarifies this is not acceptable. | No change | No change | No change
4.1003.1a | Single-Family Homes | Insulation | Attics | Attic Ceilings | Pitched/Vaulted/Cathedralized Ceilings&mdash;Loose Fill Over | Ventilation | Venting will be continuous, if applicable | Ensure capacity to increase R-value while not altering ventilation | Adjudicated - Redline only | 2015-04-15 | 2015-04-15 | John Krigger | I don't understand the text of the specification. "If applicable" sounds like the authors were intentionally vague. | The IRC requires venting the roof cavity or installing foam insulation on the rooftop in addition to filling the cavity. Weatherization allows unvented roof cavities without rooftop foam, where local officials permit it. Roof venting is always preferred if possible and continuous soffit and ridge venting is best practice. |  | Rejected | No real expected outcome given in comment or justification | No change | No change | No change
4.1003.1c | Single-Family Homes | Insulation | Attics | Attic Ceilings | Pitched/Vaulted/Cathedralized Ceilings&mdash;Loose Fill Over | Installation | When using cellulose, stabilized product is preferred when available On roof pitches less than 6/12, loose fill cellulose can be used; on roof pitches greater than 6/12, install Insulweb baffles of the same height as the insulation every 6' across slope to prevent the loose fill insulation from sliding downward, or dense pack Dense pack The process of installing loose-fill insulation to reduce air flow and perform to a stated R-value cellulose above Insulweb stapled to the bottom (underside) of the rafters Loose fill fiberglass will only be used on a slope less than or equal to a 6/12 pitch or the slope application approved by the manufacturer, whichever is less (dense packed fiberglass at slopes greater than 6/12 may be used) Roof cavities will be insulated with loose fill according to manufacturer specifications without gaps, voids, compressions, misalignments, or wind intrusions Insulation will be installed to prescribed R-value | Ensure appropriate material and applicationInsulate to prescribed R-value | Adjudicated - Redline only | 2014-04-23 | 2014-04-23 | Darrel Tenter Tenter | Insulweb is a registered trademark and should bear the ® symbol when used. |  |  | Accepted | Clarifies SWS and achieves stated objective. | No change | When using cellulose, stabilized product is preferred when available On roof pitches less than 6/12, loose fill cellulose can be used; on roof pitches greater than 6/12, install non-woven polypropylene netting (webbing) baffles of the same height as the insulation every 6' across slope to prevent the loose fill insulation from sliding downward, or dense pack cellulose above webbing stapled to the bottom (underside) of the rafters Loose fill fiberglass will only be used on a slope less than or equal to a 6/12 pitch or the slope application approved by the manufacturer, whichever is less (dense packed fiberglass at slopes greater than 6/12 may be used) Roof cavities will be insulated with loose fill according to manufacturer specifications without gaps, voids, compressions, misalignments, or wind intrusions Insulation will be installed to prescribed R-value | No change
4.1003.2a | Single-Family Homes | Insulation | Attics | Attic Ceilings | Pitched/Vaulted/Cathedralized Ceilings&mdash;Dense Pack Over | Fill slant ceilings | Using fill tube, 100% of each cavity will be filled to a consistent density: Cellulose material will be installed to a minimum density of 3.5 pounds per cubic foot Loose fiberglass material will be installed and will be specifically approved for air flow resistance per manufacturer's recommendations The number of bags installed will be confirmed and will match the number required on the coverage chart Insulation will be verified to prevent visible air movement using chemical smoke at 50 pascals of pressure difference | Ensure complete and consistent coverage throughout ceiling planeEliminate voids and settlingMinimize framing cavity air flows | Adjudicated - Redline only | 2014-07-09 | 2014-07-09 | Michael Furze | Insulation will be verified to prevent visible air movement at 50 pascals of pressure difference. | The cost of transporting Chemical smoke through the air makes the product cost prohibitive for the Washington (and New MExico) programs. Alternatives need to be found. | This should decrease cost. | Accepted with modification | Specifically noting "chemical" smoke does not address the issues that Washington and New Mexico are facing. Suggestion of using the terminology "smoke/vapor generating infiltration tools" or along the lines of that should address the commenters issue. | No change | Insulation will be verified to prevent visible air movement at 50 pascals of pressure difference using chemical smoke, IR scans, or other approved verification method. | No change
4.1004.2a | Single-Family Homes | Insulation | Attics | Knee Walls | Preparation for Batt Insulation | Knee wall Knee wall Any wall between the conditioned space and the attic prep for batts | All knee walls will have a top and bottom plate or blockers installed using a rigid material Rigid material Drywall, oriented strand board, duct board, cardboard, or any other stiff product that may support the load of insulation while serving as a durable air barrier All joints, cracks, and penetrations will be sealed in finished material, including interior surface to framing connections | Eliminate bending, sagging, or movement that may result in air leakagePrevent air leakage through the top or bottom of the knee wall Knee wall Any wall between the conditioned space and the attic Create an air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary | Adjudicated - Redline only | 2014-12-08 | 2014-12-08 | Kelly Cutchin C... | Language taken from 4.1004.1. Applies to this detail as well. | When knee wall floor and walls are being insulated, the floor joist running under the knee wall will be air sealed. | It shouldn't. People should be doing this already. | Accepted | Clarifies SWS and achieves stated objective. | No change | All knee walls will have a top and bottom plate or blockers installed using a rigid material Rigid material Drywall, oriented strand board, duct board, cardboard, or any other stiff product that may support the load of insulation while serving as a durable air barrier All joints, cracks, and penetrations will be sealed in finished material, including interior surface to framing connections When knee wall floor and walls are being insulated, the floor joist running under the knee wall will be air sealed. | No change
4.1004.5b | Single-Family Homes | Insulation | Attics | Knee Walls | Knee Walls and Gable End Walls&mdash;Preparation for and Installation of Spray Polyurethane Foam (SPF) | Installation | Insulation will be installed to prescribed R-valueUsing SPF SPF Spray polyurethane foam application, SPF SPF Spray polyurethane foam will be applied to desired thickness onto substrate material from top to bottom plate between studs using pass thickness maximum in accordance with manufacturer specificationsIn colder climates ( IECC IECC International Energy Conservation Code Zones 5-8), the SPF SPF Spray polyurethane foam will be installed to a thickness of at least Class II vapor retarder Vapor retarder A material that slows the passage of water vapor and contains a perm rating above 1 or have at least Class II vapor retarder Vapor retarder A material that slows the passage of water vapor and contains a perm rating above 1 coating or covering in direct contact with the interior of the SPF SPF Spray polyurethane foam | Eliminate cracks, gaps, and voids Minimize framing cavity air flows Minimize moisture migration and unwanted condensation in insulation (vapor retarders)Ensure alignment of insulation and air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary | Adjudicated - Redline only | 2014-04-22 | 2014-04-22 | John Krigger | This standard seem to assume that we're creating a cathedralized attic or else why would we insulate the gable-end wall? Is that the intent of this detail? |  |  | Rejected | SWS does not dictate surfaces to insulate. This SWS applies IF you are insulating Knee Walls or Gable End walls with SPF insulation. No updates needed. | No change | No change | No change
4.1005.2c | Single-Family Homes | Insulation | Attics | Attic Floors | Accessible Floors&mdash;Loose Fill Installation | Installation | All insulation will be installed to the depth indicated on the manufacturer coverage chart for desired R-value | Reduce heating and air conditioning costsImprove comfortMinimize noise | Adjudicated - Redline only | 2014-08-08 | 2014-08-08 | Adrian Correa | The standard as stated does not conform to manufacturer instructions for application of their product. See Greenfiber Attic card, PM-6.3-24 Rev F 01/13, on manufacturer's web site. Loose fill insulation may be installed at varying densities. The manufacturer warrants R-value at a certain temperature only if the density indicated is met. Calculations of density may be stated as indicated depth and minimum bags per 1,000 sq. ft., or as indicated depth and maximum coverage area per bag, etc. This standard as currently written ignores the installed density of loose fill cellulose insulation and assumes installed depth is the only factor at work to ensure desired R-value | All insulation will be installed to the minimum unsettled depth and the maximum coverage per bag for desired R-value indicated on the manufacturer's coverage chart. | This change may cause an insignificant cost in implementation until all applicators understand the factors by which their work is judged. | Accepted | Clarifies SWS and achieves stated objective. | No change | All insulation will be installed to the minimum unsettled depth and the maximum coverage per bag to reach a consistent depth for desired R-value indicated on the manufacturer's coverage chart. | No change
4.1005.3c | Single-Family Homes | Insulation | Attics | Attic Floors | Accessible Floors&mdash;Batt Insulation Over Existing Insulation | Insulation | A dated receipt signed by the installer will be provided that includes:Coverage areaThicknessR-value | Document job completion to contract specificationsConfirm amount of insulation installedEnsure ability to match bags required for total area completedComply with 16 CFR 460.17 | Adjudicated - Redline only | 2014-12-04 | 2014-12-04 | Scott Kashuba | I believe an error was made with the last change- should have changed 4.1005.3e not 4.1005.3c | I believe this language should be in 4.1005.3e The original language should be here that was removed Date Detail/Specification Previous Language 07-17-2014 4.1005.3c Specifications:Batts will be installed in accordance with manufacturer specifications without gaps, voids, compressions, misalignments, or wind intrusionsInsulation will be installed to prescribed R-value 07-17-2014 4.1005.3c Objectives:Insulate to prescribed R-value | No | Accepted | Clarifies SWS and achieves stated objective. | Insulation | Batts will be installed in accordance with manufacturer specifications without gaps, voids, compressions, misalignments, or wind intrusions Insulation will be installed to prescribed R-value | Insulate to prescribed R-value
4.1005.3e | Single-Family Homes | Insulation | Attics | Attic Floors | Accessible Floors&mdash;Batt Insulation Over Existing Insulation | Insulation | A dated receipt signed by the installer will be provided that includes:Coverage areaThicknessR-value | Document job completion to contract specificationsConfirm amount of insulation installedEnsure ability to match bags required for total area completedComply with 16 CFR 460.17 | Adjudicated - Redline only | 2014-12-04 | 2014-12-04 | Scott Kashuba | See above | regarding the previous comment I submitted. If the changes are what were intended (probably were) then the title needs changed from "Insulation" to "Onsite documentation" | No | Accepted | Changed title row for 4.1005.3e to "Onsite documentation" | Onsite documentation | A dated receipt signed by the installer will be provided that includes: Coverage area Thickness R-value | Document job completion to contract specifications Confirm amount of insulation installed Ensure ability to match bags required for total area completed Comply with 16 CFR 460.17
4.1005.6a | Single-Family Homes | Insulation | Attics | Attic Floors | Enclosed Attic Storage Platform Floor&mdash;Dense Pack Installation | Fill floors | Each cavity will be 100% filled to consistent density: Cellulose material will be installed to a minimum density of 3.5 pounds per cubic foot. Loose fiberglass material will be installed and will be specifically approved for air flow resistance to a minimum density per the manufacturer's recommendations The number of bags installed will be confirmed and will match the number required on the coverage chart Insulation will be verified to prevent visible air movement using chemical smoke at 50 pascals of pressure difference | Eliminate voids and settling Minimize framing cavity air flows | Adjudicated - Redline only | 2014-04-22 | 2014-04-22 | John Krigger | I like this standard because it specifies density and says to use fiberglass that can achieve that density. I wouldn't count on the typical coverage chart or manufacturers' specifications for guidance like you do in some other details. I might prefer a medium pack for this type of assembly to limit the pressure on the ceiling. Could we have densities for open blow, medium pack, and dense pack? |  |  | Accepted | Clarifies measure to reduce blowing out walls | No change | Each cavity will be 100% filled to consistent density: Cellulose material will be installed to a minimum density of 3.5 pounds per cubic foot or to a maximum density structurally allowable Loose fiberglass material will be installed and will be specifically approved for air flow resistance to a minimum density per the manufacturer's recommendations The number of bags installed will be confirmed and will match the number required on the coverage chart Insulation will be verified to prevent visible air movement using chemical smoke at 50 pascals of pressure difference | No change
4.1005.6c | Single-Family Homes | Insulation | Attics | Attic Floors | Enclosed Attic Storage Platform Floor&mdash;Dense Pack Installation | Onsite documentation | A dated receipt signed by the installer will be provided that includes:Coverage areaThicknessR-value | Document job completion to contract specificationsConfirm amount of insulation installedComply with 16 CFR 460.17 | Adjudicated - Redline only | 2014-04-22 | 2014-04-22 | John Krigger | Could you explain the different documentation requirements in its own section and listing what type of assembly requires what type of documentation. We don't expect the reader to have a copy of 16m CFR 460 do we? I see a variety of stated requirements and don't understand why they are different. |  |  | Rejected | Installer doesn't need copy of 16 CFR 460. Requirements are listed in the spec. Requirements vary slightly by insulation type. | No change | No change | No change
4.1005.7c | Single-Family Homes | Insulation | Attics | Attic Floors | Attic Floor&mdash;Preparation and Installation of Spray Polyurethane Foam (SPF) | Safety | Insulation will not be allowed on top of non- IC IC Insulation contact rated can light Can light A light fixture (or can) that is recessed into the ceiling boxes or between a heat-generating appliance and a dam, unless material is rated for co+H9ntact with heat-generating sources | Prevent a fire hazard | Adjudicated - Redline only | 2014-04-22 | 2014-04-22 | John Krigger | Spray foam should never be installed over light fixtures. First the R-value and direct contact can overheat the fixture causing a fire hazard or cycling the safety switch on an IC rated device. Second the temperature limit of the foam is likely to be exceeded and the foam may outgas and degrade. |  |  | Accepted | Prevent a fire hazard | No change | Spray foam should never be installed over light fixtures regardless of if fixture is rated for IC or not. Nor between a heat-generating appliance and a dam, unless material is rated for contact with heat-generating sources. | No change
4.1006.1a | Single-Family Homes | Insulation | Attics | Attic Openings | Pull-Down Stairs | Installation | Hatches will be insulated to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assemblyPull-down stair rough opening will be surrounded with a durable dam that is higher than the level of the attic floor insulationCounter-weights should be considered to ease accessibility for excessively heavy hatches | Achieve uniform R-valuePrevent loose insulation from entering the living area | Adjudicated - Redline only | 2014-06-13 | 2014-06-13 | CARL Raben | 6.11 |  |  | Rejected | No comment submitted. | No change | No change | No change
4.1006.1d | Single-Family Homes | Insulation | Attics | Attic Openings | Pull-Down Stairs | Occupant education | A dated receipt signed by the installer will be provided that includes:Coverage areaThicknessR-value | Document job completion to contract specificationsConfirm amount of insulation installedComply with 16 CFR 460.17 | Adjudicated - Redline only | 2014-12-04 | 2014-12-04 | Scott Kashuba | See above | to be consistent the title should be "Onsite documentation" | No | Accepted | Clarifies SWS and achieves stated objective. | Onsite documentation | No change | No change
4.1006.2b | Single-Family Homes | Insulation | Attics | Attic Openings | Access Doors and Hatches | Sealing | Access hatch frames will be sealed using caulk, gasket, weather-strip, or otherwise sealed with an air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary material, suitable film, or solid material Options will include installing a latch or lock or frictionally engaged components of a pre-fabricated unit above the opening that do not require a latch The measure must include a protective baffle or insulation barrier | Prevent air leakage | Adjudicated - Redline only | 2014-08-05 | 2014-08-05 | Judith Darst | Follow-up question: Our current spec calls for "tight-fitting" so as long as the hatch is snug and held in by gravity, this complies without a latch. For some hatch configurations, it will be difficult to install a latch and could possibly create an air leakage problem. | Question: What do you mean by "frictionally engaged components?" Is "tight fitting" and frictionally engaged" the same? Does gravity comply with "frictionally engaged?" | No, looking for clarification. | Accepted | Removed pre-fabricated language | No change | Access hatch frames will be sealed using caulk, gasket, weather-strip, or otherwise sealed with an air barrier material, suitable film, or solid material Options will include installing a latch or lock or frictionally engaged components that do not require a latch The measure must include a protective baffle or insulation barrier | No change
4.1006.2e | Single-Family Homes | Insulation | Attics | Attic Openings | Access Doors and Hatches | Occupant education | A dated receipt signed by the installer will be provided that includes:Coverage areaThicknessR-value | Document job completion to contract specificationsConfirm amount of insulation installedComply with 16 CFR 460.17 | Adjudicated - Redline only | 2014-12-04 | 2014-12-04 | Scott Kashuba | see above | Title should be "Onsite documentation" for consistency | no | Accepted | Clarifies SWS and achieves stated objective. | Onsite documentation | No change | No change
4.1006.3a | Single-Family Homes | Insulation | Attics | Attic Openings | Whole-House Fan | Installation | Sides of fan insulation box assembly will be insulated to the same R-value as adjoining insulated assembly | Insulate to prescribed R-value | Adjudicated - Redline only | 2014-04-22 | 2014-04-22 | John Krigger | Can we really get an R-40 out of movable insulation? I'm assuming that this box assembly is movable insulation but this should be stated. |  |  | Rejected | R-40 of movable insulation is possible; commenter's outcome was unclear | No change | No change | No change
4.1088.1a | Single-Family Homes | Insulation | Attics | Special Considerations | Attic Ventilation | Air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary and thermal boundary Thermal boundary The separation between the interior and exterior environments of a building that slows heat flow | Attic ventilation will be recommended or installed if local code requires attic ventilation during weatherization or retrofits The presence of an effective air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary and thermal boundary Thermal boundary The separation between the interior and exterior environments of a building that slows heat flow between the attic and the living space must be verified and appropriate attic sealing and proper insulation is specified as part of the scope of work | Ensure presence of continuous air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary and thermal boundary Thermal boundary The separation between the interior and exterior environments of a building that slows heat flow | Adjudicated - Redline only | 2014-04-22 | 2014-04-22 | John Krigger | This is one of the details where I don't really understand the trigger. Do you really want a weatherization crew to install more attic ventilation if the attic has only 3/4 of the code-required ventilation? Can air leakage into and out of the attic count? What about climates with humid or very rainy weather is common? When do I need to install more attic ventilation? When is cutting a hole in the roof more of a risk than just leaving an under-ventilated attic alone? |  |  | Rejected | local codes will always supersede prescriptive specifications within program manuals and field guides. If local code requires that additional ventilation be installed in an attic based upon the work being performed then local code shall be followed. | No change | No change | No change
4.1088.8b | Multifamily Homes | Insulation | Attics | Special Considerations | Installation/Correction of Unconditioned Attic Ventilation | Air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary and thermal boundary Thermal boundary The separation between the interior and exterior environments of a building that slows heat flow | Attic ventilation will be recommended or installed only if: The presence of an effective air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary and thermal boundary Thermal boundary The separation between the interior and exterior environments of a building that slows heat flow between the attic and the living space is verified Appropriate attic sealing and proper insulation is specified as part of the work scope Ignition and thermal boundaries are provided when foam plastic materials are used | Ensure presence of continuous air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary and thermal boundary Thermal boundary The separation between the interior and exterior environments of a building that slows heat flow | Adjudicated - Redline only | 2014-07-14 | 2014-07-14 | John Krigger | The authors mean barrier not boundary. | Ignition and thermal "barriers" are provided ... |  | Accepted | Clarifies SWS and achieves stated objective. | No change | Attic ventilation will be recommended or installed only if: The presence of an effective air barrier and thermal boundary between the attic and the living space is verified Appropriate attic sealing and proper insulation is specified as part of the work scope Ignition barrier and thermal boundaries are provided when foam plastic materials are used | No change
4.1101.1a | Single-Family Homes | Insulation | Walls | Preparation | Exterior Wall Dense Packing | Preparation | Lead and asbestos safety procedures will be followedCavities will be free of hazards, intact, and able to support dense pack Dense pack The process of installing loose-fill insulation to reduce air flow and perform to a stated R-value pressuresDrilling hazards (e.g., wiring, venting, fuel piping) will be locatedBlocking will be installed around:All openings to inside crawl space and basement for fibrous materialHigh temperature fire-rated materialsWiring and electrical hazardsHeat sourcesAccess to exterior wall cavities will be gained, sheathing will be drilled as needed and probed to locate each cavity, wall studs, and blockersInterior will be masked and dust controlled during drilling when accessing from interiorElectricity supply will be confirmed and will support blowing machine power demandBlowing machine pressure test will be performed with air on full, feed off, agitator running, and gate closedHose outlet pressure will be at least 80 IWC IWC Inches of water column or 2.9 psi Psi Pounds per square inch for cellulose insulation; for other types of dense pack Dense pack The process of installing loose-fill insulation to reduce air flow and perform to a stated R-value insulation, check manufacturer specification for blowing machine set up | Prevent damage to houseProvide a clean work spaceProvide thorough access to allow 100% coverageEnsure proper equipment and process results in consistent densityPrevent settling and retard air flow through cavitiesProtect worker and occupant health | Adjudicated - Redline only | 2014-09-09 | 2014-09-09 | Stephen Lommele | Test justification and substantiation. | Test language. | Test no. | Rejected | Test of system, not comment on SWS. | No change | No change | No change
4.1101.3b | Single-Family Homes | Insulation | Walls | Preparation | Exterior Wall Spray Polyurethane Foam (SPF)&mdash;Masking and Surface Preparation | Substrate repair | Cracks, gaps, and holes in the substrate will be covered or sealed in accordance with manufacturer specifications with appropriate material | Prevent waste of SPF SPF Spray polyurethane foam Prevent overspray into adjacent areas | Adjudicated - Redline only | 2014-04-22 | 2014-04-22 | John Krigger | I don't quite understand what surface we're installing SPF to in this standard. Interior, exterior, open cavity, or to a finished surface? |  |  | Rejected | SWS is clarifying objectives if you are installing SPF on an exterior wall. Auditor will determine which particular surfaces you are applying SPF to, not the SWS. | No change | No change | No change
4.1102.1d | Single-Family Homes | Insulation | Walls | Accessible Walls | Open-Cavity Wall Insulation&mdash;General | Occupant education | A dated receipt signed by the installer will be provided that includes:Insulation typeCoverage areaR-valueInstalled thickness and settled thickness (settled thickness required for loose-fill only)Number of bags installed in accordance with manufacturer specifications (for loose-fill only) | Document job completion to contract specificationsConfirm amount of insulation installedComply with 16 CFR 460.17 | Adjudicated - Redline only | 2014-12-04 | 2014-12-04 | Scott Kashuba | see above | Title "Onsite documentation" | no | Accepted | Clarifies SWS and achieves stated objective. | Onsite documentation | No change | No change
4.1103.1a | Single-Family Homes | Insulation | Walls | Enclosed Walls | Dense Pack Exterior Walls | Exterior dense pack Dense pack The process of installing loose-fill insulation to reduce air flow and perform to a stated R-value | Using fill tube, 100% of each cavity will be filled to a consistent density: Cellulose insulation used in an enclosed cavity will be installed at 3.5 pounds per cubic foot or greater density Blown fiberglass, mineral fiber, or rock and slag wool used in an enclosed cavity will be installed at or above the manufacturer recommended density to limit air flow that corresponds to an air permeance value of 3.5 cfm CFM Cubic feet per minute /sq. ft. at 50 pascals, as measured using BPI BPI Building Performance Institute, www.bpi.org -102 "Standard for Air Resistance of Thermal Insulation Used in Retrofit Cavity Applications – Material Specification" or ASTM ASTM ASTM International, www.astm.org C 522, E 283, or E 2178; the number of bags installed will be confirmed and will match the number required on the coverage chart Insulation will be verified to prevent visible air movement using chemical smoke at 50 pascals of pressure difference | Eliminate voids and settling Minimize framing cavity air flows | Adjudicated - Redline only | 2014-12-15 | 2014-12-15 | Kelly Cutchin C... | The job isn't done until it's patched and cleaned up, so that step should be included here. I don't think it's covered anywhere else in the SWS. | Add a row to this detail describing patching options. We should include something about patching interior walls with plugs/plaster or chair rail trim and patching exterior feed holes with plugs and caulk or siding to keep moisture out. | No, it's already part of the job, just not written down here yet. | Accepted | Clarifies SWS and achieves stated objective. | No change | Using fill tube, 100% of each cavity will be filled to a consistent density: Cellulose insulation used in an enclosed cavity will be installed at 3.5 pounds per cubic foot or greater density Blown fiberglass, mineral fiber, or rock and slag wool used in an enclosed cavity will be installed at or above the manufacturer recommended density to limit air flow that corresponds to an air permeance value of 3.5 cfm /sq. ft. at 50 pascals, as measured using BPI -102 "Standard for Air Resistance of Thermal Insulation Used in Retrofit Cavity Applications – Material Specification" or ASTM C 522, E 283, or E 2178; the number of bags installed will be confirmed and will match the number required on the coverage chart All holes and penetrations will be plugged and/or sealed Insulation will be verified to prevent visible air movement using chemical smoke at 50 pascals of pressure difference | No change
4.1103.2c | Single-Family Homes | Insulation | Walls | Enclosed Walls | Additional Exterior Wall Cavities | Dense packing | Using fill tube, 100% of each cavity will be filled to a consistent density:Cellulose insulation used in an enclosed cavity will be installed at 3.5 pounds per cubic foot or greater densityBlown fiberglass, mineral fiber, or rock and slag wool used in an enclosed cavity will be installed at or above the manufacturer recommended density to limit airflow that corresponds to an air permeance value of 3.5 cfm CFM Cubic feet per minute /sq. ft. at 50 pascals, as measured using BPI BPI Building Performance Institute, www.bpi.org -102 "Standard for Air Resistance of Thermal Insulation Used in Retrofit Cavity Applications—Material Specification" or ASTM ASTM ASTM International, www.astm.org C 522, E 283, or E 2178; the number of bags installed will be confirmed and will match the number required on the coverage chartInsulation will be verified to prevent visible air movement using chemical smoke at 50 pascals of pressure difference | Eliminate voids and settlingMinimize framing cavity air flows | Adjudicated - Redline only | 2015-04-21 | 2015-04-21 | Kelly Cutchin C... | The language isn't related to dense pack, rather the quality control of that dense pack. Belongs in the row below. | Remove this text from the bottom: Insulation will be verified to prevent visible air movement using chemical smoke at 50 pascals of pressure difference. This should be added to the row below for quality control as an either/or option. | No. | Accepted | Clarifies SWS and achieves stated objective. | No change | Using fill tube, 100% of each cavity will be filled to a consistent density: Cellulose insulation used in an enclosed cavity will be installed at 3.5 pounds per cubic foot or greater density Blown fiberglass, mineral fiber, or rock and slag wool used in an enclosed cavity will be installed at or above the manufacturer recommended density to limit airflow that corresponds to an air permeance value of 3.5 cfm /sq. ft. at 50 pascals, as measured using BPI -102 "Standard for Air Resistance of Thermal Insulation Used in Retrofit Cavity Applications—Material Specification" or ASTM C 522, E 283, or E 2178; the number of bags installed will be confirmed and will match the number required on the coverage chart | No change
4.1103.4a | Multifamily Homes | Insulation | Walls | Enclosed Walls | Dense Packing Blown Insulation | Worker safety | All worker safety specifications will be in accordance with SWS 2.0100.3 Worker Safety Lead safety procedures in buildings built before 1980 will be followed | Ensure worker safety, especially in regard to fall protection considerations and contaminants found in demolition, such as asbestos, lead, polychlorinated biphenyls, etc. | Adjudicated - Redline only | 2014-08-05 | 2014-08-05 | Judith Darst | All of our lead safety procedures are based on the year 1978. | Question: Why does this spec (4.1103.4a) refer to 1980: "Lead safety procedures in buildings built before 1980 will be followed?" | No, looking for clarification. | Accepted with modification | Clarifies SWS and achieves stated objective. | No change | All worker safety specifications will be in accordance with SWS 2.0100.3 Worker Safety Lead safety procedures in buildings built before 1978 will be followed, unless approved testing method proves absence of lead based paint in surfaces that will be disturbed | No change
4.1303.1d | Manufactured Housing | Insulation | Floors | Manufactured Housing Floor Cavity Insulation | Insulation of Floor Cavity with Blown Material | Materials | Flame spread index of selected materials will not exceed 25 with an accompanying smoke-developed index not to exceed 450 when tested in accordance with ASTM ASTM ASTM International, www.astm.org E84 or UL UL Underwriters Laboratories 723Flame spread index of foam insulation will not exceed 75 and a smoke- developed index of no more than 450 when tested in the maximum thickness intended for use in accordance with ASTM ASTM ASTM International, www.astm.org E84 or UL UL Underwriters Laboratories 723Foam insulation will be separated from the interior of the building by an approved thermal barrier at a minimum of 1/2" gypsum or a material that is tested in accordance with the acceptance criteria of both the Temperature Transmission Fire Test and the Integrity Fire Test of NFPA NFPA National Fire Protection Association, www.nfpa.org 275Selected material will be of minimal water absorbency Selected material will be noncorrosive | Ensure durability Prevent moisture damage Fire safety will be maintained | Adjudicated - Redline only | 2014-08-05 | 2014-08-05 | Judith Darst | Follow up Questions: Does "Blown Material" refer to cellulose insulation or blown-in foam insulation? If it refers to blown-in foam insulation, then how is that distinguished from "4.1303.3 Insulation of Floor Cavity with Spray Foam Material?" | Question: Why does this spec "4.1303.1 Insulation of Floor Cavity with Blown Material" refer to "Foam insulation?" | No, looking for clarification. | Rejected | The foam insulation referred to is rigid foam board used to repair the belly to prepare it to receive the blown material | No change | No change | No change
4.1401.1a | Single-Family Homes | Insulation | Basements and Crawl Spaces | Band/Rim Joists | Band/Rim Joists&mdash;Spray Polyurethane Foam (SPF) Installation | Preparation | All band/rim joist areas will be open and accessible for SPF SPF Spray polyurethane foam applicationAll surfaces where SPF SPF Spray polyurethane foam is applied will be clean, dry, and free of contamination and degradationSubstrate surfaces will be wiped, blown, or vacuumed to be free of excessive dust and dirtGrease and oil will be removed using appropriate cleaners or solventsMoisture content of all wood substrate materials will be checked to ensure it is below 20% | Prepare all substrate surfaces for the application of SPF SPF Spray polyurethane foam | Adjudicated - Redline only | 2014-07-14 | 2014-07-14 | John Krigger | Using foam board reduces the danger of poisoning by the spray foam because less liquid foam is used. | Include other options such as foam board sealed at the edges with expanding foam. |  | Rejected | This detail specifically addresses those situations where you are using SPF for this application. It is not intended to lay out all options for band/rim joist insulation. 4.1401.2 addresses other options. | No change | No change | No change
4.1401.1b | Single-Family Homes | Insulation | Basements and Crawl Spaces | Band/Rim Joists | Band/Rim Joists&mdash;Spray Polyurethane Foam (SPF) Installation | Installation | SPF SPF Spray polyurethane foam will be applied to desired thickness, using pass thickness maximum in accordance with manufacturer specifications, onto subfloor between floor joists and all rim/band joistsWhen applied to first floor, SPF SPF Spray polyurethane foam will be continuous from subfloor surface, over band/rim joist and sill plate, and in contact with foundation belowWhen applied to second story floor or above, SPF SPF Spray polyurethane foam will be continuous from subfloor surface, over band/rim joist, and in contact with top plate below | Insulate and seal floors | Adjudicated - Redline only | 2014-07-14 | 2014-07-14 | John Krigger | People are assuming from this spec that SPF is the only way to insulate and air-seal a rim joist. You have other standards in the basement wall sections. Should the be moved to this topic or duplicated here? | Move text from other sections or duplicate so people searching for rim joist insulation find it here under this topic. |  | Rejected | 4.1401.2 addresses other options, and is listed in this same subtopic so should be easily found. | No change | No change | No change
4.1401.1b | Single-Family Homes | Insulation | Basements and Crawl Spaces | Band/Rim Joists | Band/Rim Joists&mdash;Spray Polyurethane Foam (SPF) Installation | Installation | SPF SPF Spray polyurethane foam will be applied to desired thickness, using pass thickness maximum in accordance with manufacturer specifications, onto subfloor between floor joists and all rim/band joists When applied to first floor, SPF SPF Spray polyurethane foam will be continuous from subfloor surface, over band/rim joist and sill plate, and in contact with foundation below When applied to second story floor or above, SPF SPF Spray polyurethane foam will be continuous from subfloor surface, over band/rim joist, and in contact with top plate below | Insulate and seal floors | Adjudicated - Redline only | 2015-05-13 | 2015-05-13 | Aaron Travaglini | Line #2 in the above specification is being contradicted in a following specification. the specification is 4.1402.1c. I think there needs to be some review in these 2 areas. | Again I'm not sure how the new text should read. | Not that I know of at this time. | Accepted | Clarifies SWS and achieves stated objective. | No change | SPF will be applied to desired thickness, using pass thickness maximum in accordance with manufacturer specifications, onto subfloor between floor joists and all rim/band joists When applied to first floor, SPF will be continuous from subfloor surface, over band/rim joist and sill plate, and in contact with foundation below, except as stipulated by classification 4.1402.1c When applied to second story floor or above, SPF will be continuous from subfloor surface, over band/rim joist, and in contact with top plate below | No change
4.1401.1c | Single-Family Homes | Insulation | Basements and Crawl Spaces | Band/Rim Joists | Band/Rim Joists&mdash;Spray Polyurethane Foam (SPF) Installation | Fire protection | If SPF SPF Spray polyurethane foam exceeds a thickness of 3", all SPF SPF Spray polyurethane foam will be separated from the occupied interior space of the building with an approved thermal barrier material (typically ½" or thicker gypsum wallboard or an approved thermal barrier coating)Application to rim/band joist up to 3" can be left exposed if the foam is Class I Local codes will be confirmed and followed for fire protection requirements | Provide necessary fire protection for combustible SPF SPF Spray polyurethane foam insulation | Adjudicated - Redline only | 2014-07-13 | 2014-07-13 | John Krigger | Could be confusion between vapor retarder and fire-rated assembly. Also could be interpreted as not requiring a thermal barrier for foam in a habitable space in violation of IRC R312. | Use Class I or Class A fire-rated assembly (not exactly sure of the wording) Class I could be a vapor retarder. Could be confusing. After Class I insert: "unless the space is a habitable space and then cover it with drywall or another thermal barrier." |  | Accepted | Clarifies SWS and achieves stated objective. | No change | If SPF exceeds a thickness of 3", all SPF will be separated from the occupied interior space of the building with an approved thermal barrier material (typically ½" or thicker gypsum wallboard or an approved thermal barrier coating) Application to rim/band joist up to 3" can be left exposed if the foam is Class I, unless the space is a habitable space and then cover it with drywall or another thermal barrier Local codes will be confirmed and followed for fire protection requirements | No change
4.1401.2b | Single-Family Homes | Insulation | Basements and Crawl Spaces | Band/Rim Joists | Band/Rim Joists – Insulation other than Spray Polyurethane Foam | Insulation installation | A foam-based insulation will be installed so as to create a continuous thermal and pressure boundary. If rigid insulation is used, all edges will be sealed and the insulation will be installed tightly to the wood to prevent the movement of moisture throughout the assembly. Insulation will be installed in accordance with local/national code requirements and/or manufacturer’s instructions regarding flame spread. | Improve thermal performance Prevent moisture condensation on the inside of the band joist | Adjudicated - Redline only | 2015-05-29 | 2015-05-29 | Kelly Cutchin C... | The vinyl faced fiberglass batts are often used in commercial basements, and have a standard for vapor permeance - ASTM C665-06 or current, already referenced in SWS. | Add: Or vinyl faced fiberglass batt insulation, installed tightly to the wood and sealed at all edges. | No. | Accepted | Clarifies SWS and achieves stated objective. | No change | A foam-based insulation will be installed so as to create a continuous thermal and pressure boundary or vinyl faced fiberglass batt insulation, installed tightly to the wood and sealed at all edges. If rigid insulation is used, all edges will be sealed and the insulation will be installed tightly to the wood to prevent the movement of moisture throughout the assembly. Insulation will be installed in accordance with local/national code requirements and/or manufacturer’s instructions regarding flame spread | No change
4.1402.1a | Single-Family Homes | Insulation | Basements and Crawl Spaces | Basements and Crawl Space Walls | Closed Crawl Spaces—Wall Insulation | Insulation selection | A non fibrous, fire-rated Class I insulation will be used with a minimum life expectancy of 10 years | Provide fire-safe durable insulation | Adjudicated - Redline only | 2014-03-31 | 2014-07-14 | John Krigger | This spec is vague and misses the main issues of insulating crawl space walls. What do you mean by non-absorbent and fire rated? Does non-absorbent mean no fibrous insulation: That wouldn't be a bad decision. Fiberglass only absorbs 7% water by weight but the common facings used in crawl spaces are vapor barriers, which hinder drying. Fiberglass batts aren't a bad choice for dry climates: suggest < 20 inches of precip and <60% average rh. However, the vapor-barrier facing is still a problem. I think that by fire-rated you mean 25 or less flame spread or Class I or Class A rating. Might as well mention all of these ratings. | n/a |  | Accepted | Clarifies SWS and achieves stated objective. | No change | A fire-rated insulation (25 or less flame spread or Class I or Class A) will be used with a minimum life expectancy of 10 years | Provide fire-safe, durable insulation that will not exacerbate moisture issues in the crawl space
4.1402.1a | Single-Family Homes | Insulation | Basements and Crawl Spaces | Basements and Crawl Space Walls | Closed Crawl Spaces—Wall Insulation | Insulation selection | A non fibrous, fire-rated Class I insulation will be used with a minimum life expectancy of 10 years | Provide fire-safe durable insulation | Adjudicated - Redline only | 2015-04-03 | 2015-04-03 | Kelly Cutchin C... | Last review session, I believe the language was updated to specify non-fibrous insulation. Moisture concerns led to this update but the objective was not updated. It can currently be argued that fibrous insulations meet the stated objective. | Update objectives to read: Provide fire-safe, durable insulation that will not exacerbate moisture issues in the crawl space. | Yes. Foam board is typically more expensive than batt fiberglass insulation. This was deemed acceptable in the previous update when "non-fibrous" was adopted. | Accepted | Clarifies SWS and achieves stated objective. | No change | No change | Provide fire-safe, durable insulation that will not exacerbate moisture issues in the crawl space
4.1402.1c | Single-Family Homes | Insulation | Basements and Crawl Spaces | Basements and Crawl Space Walls | Closed Crawl Spaces—Wall Insulation | Termite inspection gap | Where termite pressure exists, a 3" inspection gap will be maintained from the top of the insulation to the bottom of any wood | Allow for termite detection | Adjudicated - Redline only | 2015-05-13 | 2015-05-13 | Aaron Travaglini | I am just trying to get clarification on the above specification. There is no location to actually voice concerns or complaints. | Can you please explain what the term "termite pressure" means. If the crawlspace is intended to be insulated and air sealed how does this inspection gap help? The sill plate and foundation wall are not sealed and need to be treated. Applying urethane foam from the upper floor of the box sill down over the sill plate and continuing onto the foundation wall to create a monolithic surface is the most common practice. | The specification above is the reason the cost of installation/implementation has gone up. It is more cumbersome to treat the area now then it ever has been in the past. The main reason for the increase is the area still needs to be air sealed. We are exploring other ways to treat the area but reverting back to urethane foam over the entire area will be the easier solution. | Rejected | Termite issues vary vastly across the nation and this policy must encompass those areas | No change | No change | No change
4.1402.1d | Single-Family Homes | Insulation | Basements and Crawl Spaces | Basements and Crawl Space Walls | Closed Crawl Spaces—Wall Insulation | Attachment | Insulation will be attached with a durable connection equal to or better than manufacturer specifications | Prevent insulation from detaching from the foundation wall | Adjudicated - Redline only | 2014-07-14 | 2014-07-14 | John Krigger | Confusing and redundant wording | Insulation will be attached with a durable connection better than or equal to manufacturer specifications. |  | Accepted | Clarifies SWS and achieves stated objective. | No change | Insulation will be attached with a durable connection better than or equal to manufacturer specifications | No change
4.1402.2c | Single-Family Homes | Insulation | Basements and Crawl Spaces | Basements and Crawl Space Walls | Basement Wall Insulation&mdash;No Groundwater Leakage | Vapor permeability | When absorbent insulation materials are installed, assembly will remain vapor permeable to the interior in all climate zones except Zone 7 | Provide drying potential to the basement | Adjudicated - Redline only | 2014-07-13 | 2014-07-13 | John Krigger | Current standard all but bans foundation insulation. | Oops, I was being too optimistic in my previous comment. You would have to change "vapor permeable" to vapor "semi-impermeable" meaning Class II vapor retarder to allow the most common insulation assemblies for foundation walls. |  | Accepted | Clarifies SWS and achieves stated objective. | No change | When absorbent insulation materials are installed, assembly will remain vapor semi-impermeable to the interior in all climate zones except Zone 7 | No change
4.1402.2c | Single-Family Homes | Insulation | Basements and Crawl Spaces | Basements and Crawl Space Walls | Basement Wall Insulation&mdash;No Groundwater Leakage | Vapor permeability | When absorbent insulation materials are installed, assembly will remain vapor permeable to the interior in all climate zones except Zone 7 | Provide drying potential to the basement | Adjudicated - Redline only | 2014-07-13 | 2014-07-13 | John Krigger | Current standard all but forbids basement and crawl-space wall insulation. Vapor permeable means more than 10 perms according to ASHRAE. Unfaced fiberglass or spray fiber would be the only common insulations that would comply and they aren't durable. | Instead of "vapor permeable" insert "vapor semi-permeable". |  | Accepted | Clarifies SWS and achieves stated objective. | No change | When absorbent insulation materials are installed, assembly will remain vapor semi-impermeable to the interior in all climate zones except Zone 7 | No change
5.3003.14a | Single-Family Homes, Manufactured Housing | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Gas-Fired Appliances (LP and Natural Gas) | Place appliance in operation | Heating equipment will be placed in operation in accordance with applicable NFPA NFPA National Fire Protection Association, www.nfpa.org standards and manufacturer specifications when available | Ensure equipment: Operates as designed Operates safely Operates efficiently Is durable | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | This isn't replacement, it's evaluating existing units, right? | will be evaluated |  | Rejected | The phrasing "Place in operation" means the unit will be turned on, which is a step in overall evaluation. | No change | No change | No change
5.3003.14b | Single-Family Homes, Manufactured Housing | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Gas-Fired Appliances (LP and Natural Gas) | Gas pressure | Measurement will be verified by a certified professional in accordance with fuel type and manufacturer specifications | Ensure equipment: Operates as designed Operates safely Operates efficiently Is durable | Adjudicated - Redline only | 2015-02-16 | 2015-02-16 | John Krigger | If CO, oxygen, and gas temperature are good, I see no reason to require gas pressure measurement. Gas pressure can be in a wide range 3.2-4.5 or something like that. Clocking the meter might be necessary to discover the cause of too high or too low flue gas temperature but you couldn't learn much from gas pressure alone. | Determine the gas BTUH input by clocking the gas meter if necessary to diagnose problems with CO, flue-gas temperature, or oxygen content. |  | Accepted with modification | Measuring the gas pressure must be done by a certified professional (as stated). This should be part of an overall tuneup. | No change | If fault has been determined in the preceding steps, then measurement will be verified by a certified professional in accordance with fuel type and manufacturer specifications (move spec down to a lower number) | No change
5.3003.14e | Single-Family Homes, Manufactured Housing | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Gas-Fired Appliances (LP and Natural Gas) | Carbon monoxide ( CO CO Carbon monoxide ) in flue gas | CO CO Carbon monoxide in the undiluted flue gas will be less than 100 ppm | Ensure equipment: Operates as designed Operates safely Operates efficiently Is durable | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | This is a clear mistake or an unacceptable duality given the 200/400 ppm standard in health and safety. | Is it 100 or 200??? |  | Accepted with modification | Align with BPI 1200 | No change | CO in the undiluted flue gas will be less than 400 ppm air-free | No change
5.3003.14e | Single-Family Homes, Manufactured Housing | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Gas-Fired Appliances (LP and Natural Gas) | Carbon monoxide ( CO CO Carbon monoxide ) in flue gas | CO CO Carbon monoxide in the undiluted flue gas will be less than 100 ppm | Ensure equipment: Operates as designed Operates safely Operates efficiently Is durable | Adjudicated - Redline only | 2014-12-19 | 2014-12-19 | Kelly Cutchin C... | As measured and air free readings give different CO levels for the same conditions, so we need to state which measurement is meant. | Clarify if the 100 ppm limit is as measured or air free. | No. | Accepted with modification | Align with BPI 1200 | No change | CO in the undiluted flue gas will be less than 400 ppm air-free | No change
5.3003.14f | Single-Family Homes, Manufactured Housing | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Gas-Fired Appliances (LP and Natural Gas) | Testing/inspection holes | All testing and inspection holes will be sealed with manufacturer approved materials | Ensure equipment: Operates as designed Operates safely Operates efficiently Is durable | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | Too vague to be useful. | Would need considerable additional language. |  | Rejected | The SWS spec is to seal holes with appropriate materials. This can be confirmed by inspection. | No change | No change | No change
5.3003.15h | Manufactured Housing | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Oil-Fired Appliances | Excess combustion air | Excess combustion air will be calculated and shown to be in accordance with industry manuals (e.g., Testo, Bacharach) | Ensure equipment: Operates as designed Operates safely Operates efficiently Is durable | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | Industry manuals: what do you mean? A lot of equipment specs don't include SSE, O2, flue gas temp. | Accepted standards?? Why don't you suggest some? |  | Accepted with modification | Users of the SWS are not expected to be qualified to act upon adjustments of efficiency. This should be part of a general tune-up. | No change | Excess air will be minimized in accordance with industry best practices | No change
5.3003.15i | Manufactured Housing | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Oil-Fired Appliances | CO CO Carbon monoxide in flue gas | CO CO Carbon monoxide in the undiluted flue gas will be less than 100 ppm | Ensure equipment: Operates as designed Operates safely Operates efficiently Is durable | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | I can't justify having 100 ppm here with mostly sealed-combustion appliances (mobile home) when you spec 200 for open-combustion in site-built homes. | 100/200 dilemma continued. |  | Accepted with modification | Align with BPI 1200 | No change | CO in the undiluted flue gas will be less than 400 ppm air-free | No change
5.3003.15i | Manufactured Housing | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Oil-Fired Appliances | CO CO Carbon monoxide in flue gas |  |  | Adjudicated - Redline only | 2015-12-15 | 2015-12-15 | Kelly Cutchin C... | Align with BPI 1200. Note - This is already in the table of comments to be sent to committee. It should be pulled out and addressed along with the combustion safety updates. | CO in the undiluted flue gas will be less than 400 ppm air free. |  | Accepted with modification | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): The document has been updated to "400 ppm air-free" to align with BPI 1200. In addition, this same language was updated in 5.3003.14e, for both single family and manufactured housing.
5.3003.2a | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Oil-Fired Appliances | Oil system: nozzle size | Nozzle size will be correct for design input and within equipment firing rate of the heating system manufacturer | Ensure equipment operates as designed Ensure equipment operates safely Ensure equipment operates efficientlyEnsure equipment is durable | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | Be consistent. | Combine single-family with mobile with tabs. Confusing as is given your convention of using tabs. Allows for comparison. |  | Further investigation required | No language change - add tab for to 5.3003.15 forMH Two issues: 1. checking the nozzle size is not expected from the users of the SWS. 2. Commenter has a good point about the lack of a tab for MH unless there are never oil burners in manufactured homes. | No change | No change | No change
5.3003.2a | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Oil-Fired Appliances | Oil system: nozzle size | Nozzle size will be correct for design input and within equipment firing rate of the heating system manufacturer | Ensure equipment operates as designed Ensure equipment operates safely Ensure equipment operates efficientlyEnsure equipment is durable | Adjudicated - Redline only | 2016-07-27 | 2016-07-27 | Charles Kurnik | Under committee guidance, this entire Detail has been reorganized to reflect the order in which the work should occur, and to reference ACCA 5.Additional Specification rows have also been added. | New text to be provided in 2016 redline version |  | Accepted | Added new specification to clarify | Oil System: filter | Filter will be present, clean, and leak free | Ensure oil filter is present and functional
5.3003.2d | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Oil-Fired Appliances | Oil system: smoke test (This test must be conducted before any combustion testing is completed) | Smoke spot reading will be in accordance with burner manufacturer specificationsIf smoke test is more than actionable levels, specify a clean and tune | Ensure equipment operates as designed Ensure equipment operates safely Ensure equipment operates efficientlyEnsure equipment is durable | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | Current standard too vague to be useful or credible. | Smoke spot should be less than 1. |  | Rejected | Intent of SWS is for smoke spot to be in accordance with burner manufacturer specifications | No change | No change | No change
5.3003.2d | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Oil-Fired Appliances | Oil system: smoke test (This test must be conducted before any combustion testing is completed) | Smoke spot reading will be in accordance with burner manufacturer specificationsIf smoke test is more than actionable levels, specify a clean and tune | Ensure equipment operates as designed Ensure equipment operates safely Ensure equipment operates efficientlyEnsure equipment is durable | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | Do this before taking steady-state efficiency. | Place before current 2c |  | Accepted with modification | No language change - switch order with 5.3003.2c Number of issues here: No comment was made on 5.3003.2b regarding a measurement of oil pressure which is not expected from users and probably should be removed; Second, commenter has a point that the smoke spot test should be done before SSE especially if 5.3003.2d is going to remain in place. | No change | No change | No change
5.3003.2f | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Oil-Fired Appliances | Carbon dioxide and oxygen | Measurement will be verified in accordance with industry manuals and manufacturer specifications | Ensure equipment operates as designed Ensure equipment operates safely Ensure equipment operates efficientlyEnsure equipment is durable | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | I believe that all current testers measure oxygen. Why mention CO2? Steady-state efficiency handles this anyway. | If steady-state is out of range, notice the O2 reading to see if it is high or low. |  | Rejected | Not enough detail in comment, please clarify | No change | No change | No change
5.3003.2g | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Oil-Fired Appliances | Excess air | Excess air will be calculated and shown to be in accordance with manufacturer specifications | Ensure equipment operates as designed Ensure equipment operates safely Ensure equipment operates efficientlyEnsure equipment is durable | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | Delete standard. It is redundant with previous mentioning O2. | Delete, if you analyze O2 it is the same as analyzing excess air. |  | Accepted with modification | Language changed to clarify SWS and achieves stated objective. | No change | Excess air will be minimized in accordance with industry best practices | No change
5.3003.2h | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Oil-Fired Appliances | CO CO Carbon monoxide in flue gas | Undiluted flue gases will be checked with a calibrated combustion analyzerFor CO CO Carbon monoxide levels exceeding 200 ppm as measured, or 400 ppm air-free measurement, service will be provided to reduce CO CO Carbon monoxide to below these levels (unless CO CO Carbon monoxide measurement is within manufacturer specifications) | Ensure equipment operates as designed Ensure equipment operates safely Ensure equipment operates efficientlyEnsure equipment is durable | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | Oil is usually adjustable to below 100 ppm and the argument is good for doing so. Less soot. | Make up your mind about 100/200 ppm |  | Accepted with modification | Adjust the levels to align with BPI 1200 | No change | Undiluted flue gases will be checked with a calibrated combustion analyzer For CO levels exceeding 400 ppm air-free measurement, service will be provided to reduce CO to below these levels (unless CO measurement is within manufacturer specifications). Adjustment to achieve CO reading of less than 200 air-free shall be attempted | Ensure equipment operates as designed Ensure equipment operates safely Ensure equipment operates efficientlyEnsure equipment is durable Reduce soot.
5.3003.3a | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Evaluating Air Flow | Total air flow | Total system air flow will be measured by:Temperature riseFlow plateFan depressurization device (e.g., Duct Blaster, DucTester) | Ensure equipment operates as designed Ensure equipment operates efficiently Ensure equipment provides comfort Ensure equipment operates safely Ensure equipment is durable | Adjudicated - Redline only | 2014-04-23 | 2014-04-23 | Darrel Tenter Tenter | Duct Blaster and DucTester are both registered trademarks and should bear the ® symbol when used. |  |  | Accepted with modification | Trademarks are important to protect. | No change | Total system air flow will be measured by one of the following methods: Temperature riseFlow plateFan depressurization device (e.g., Duct Blaster®, DucTester®) | No change
5.3003.3a | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Evaluating Air Flow | Total air flow | Total system air flow will be measured by:Temperature riseFlow plateFan depressurization device (e.g., Duct Blaster, DucTester) | Ensure equipment operates as designed Ensure equipment operates efficiently Ensure equipment provides comfort Ensure equipment operates safely Ensure equipment is durable | Adjudicated - Redline only | 2015-06-03 | 2015-06-03 | Kelly Cutchin C... | All 3 measurements aren't required to meet the stated objectives, but as written the SWS could be interpreted to mean you must do all 3 tests. | Total system air flow will be measured by one of the following methods: | No. | Accept | Clarifies SWS and achieves stated objective. | No change | Total system air flow will be measured by one of the following methods: Temperature riseFlow plateFan depressurization device (e.g., Duct Blaster®, DucTester®) | No change
5.3003.5a | Manufactured Housing | Heating and Cooling | Forced Air | System Assessment and Maintenance | Refrigerant Line Inspection | Insulation | All liquid refrigerant lines will be insulated to a minimum of R-4Vapor or high side lines will not be insulated unless specified by the equipment's manufacturerSuction lines will be insulated to a minimum of R-4For mixed humid, hot humid, and marine climates, heating and cooling refrigerant lines will be insulated | Ensure refrigerant lines do not gain excessive heatPrevent energy loss and condensation | Adjudicated - Redline only | 2015-08-10 | 2015-08-10 | CHP Energy Solutions | The liquid refrigerant line is the the high side (small tube) which is usually warm since it is under pressure and a high temp liquid. The original specification indicates that the vapor line is the high-side line, which is entirely incorrect. The spec also, by mistakenly calling for the liquid and suction lines to be insulated, calls for both lines in the set to be insulated. This clarification is needed to make sure that insulation is not being installed where it doesn't need to be. The objective change is to reflect the actual reason for insulating the suction line which is to prevent condensation from occurring inside the building cavities on the exterior surfaces of the cold vapor line. This is because with the above adjustments the proper lines will already be insulated and this additional sentence is unnecessary and creates the debate over what climate zone you are "really" in. The reference to the manufacturer's instructions will make sure the high side line is insulated when necessary. | Remove the requirement that "all liquid refrigerant lines will be insulated to a minimum of R4" since only the Suction line (low pressure, vapor line) must be insulated unless the manufacturer calls for it. The new spec should read: "All suction or vapor refrigerant lines, will be insulated to a minimum of R-4" "High-side or liquid refrigerant lines will not be insulated unless specified by the equipment's manufacturer" The objective should also be changed to indicate that this is to prevent condensation from the vapor line. It should now read: "Ensure refrigerant lines do not gain excessive heat, or cause condensation to occur inside the building envelope" Also remove the last sentence about mixed humid, hot humid, and marine climates.... | No cost increase is expected. It may lead to a reduction in cost, as the spec is currently calling for both lines to be insulated. | Accept | Clarifies SWS and achieves stated objective. | No change | All suction or vapor refrigerant lines, will be insulated to a minimum of R-4 High-side or liquid refrigerant lines will not be insulated unless specified by the equipment's manufacturer | Ensure refrigerant lines do not gain excessive heat, or cause condensation to occur inside the building envelope
5.3003.5a | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Refrigerant Line Inspection | Insulation | All liquid refrigerant lines will be insulated to a minimum of R-4Vapor or high side lines will not be insulated unless specified by the equipment's manufacturerSuction lines will be insulated to a minimum of R-4 | Ensure refrigerant lines do not gain excessive heat | Adjudicated - Redline only | 2015-08-10 | 2015-08-10 | CHP Energy Solutions | The liquid refrigerant line is the the high side (small tube) which is usually warm since it is under pressure and a high temp liquid. The original specification indicates that the vapor line is the high-side line, which is entirely incorrect. The spec also, by mistakenly calling for the liquid and suction lines to be insulated, calls for both lines in the set to be insulated. This clarification is needed to make sure that insulation is not being installed where it doesn't need to be. The objective change is to reflect the actual reason for insulating the suction line which is to prevent condensation from occurring inside the building cavities on the exterior surfaces of the cold vapor line. | Remove the requirement that "all liquid refrigerant lines will be insulated to a minimum of R4" since only the Suction line (low pressure, vapor line) must be insulated unless the manufacturer calls for it. The new spec should read: "All suction or vapor refrigerant lines, will be insulated to a minimum of R-4" "High-side or liquid refrigerant lines will not be insulated unless specified by the equipment's manufacturer" The objective should also be changed to indicate that this is to prevent condensation from the vapor line. It should now read: "Ensure refrigerant lines do not gain excessive heat, or cause condensation to occur inside the building envelope" | No cost increase is expected. It may lead to a reduction in cost, as the spec is currently calling for both lines to be insulated. | Rejected (duplicate) | Duplicate comment, previosuly accepted | No change | No change | No change
5.3102.1a | Multifamily Homes | Heating and Cooling | Hydronic Heating (Hot Water and Steam) | Equipment Installation | Replacement with Hot Water Boiler | Assessment | Confirmation of the scope of work will be made for the following: ClearancesProper drainage in boiler roomFlue/chimney conditionsElectrical capacityOil/gas availabilityPiping connections | Verify scope of work | Adjudicated - Redline only | 2014-06-03 | 2014-06-03 | Juan Saiz | Tested co after water heart was install reading were 0 and reading tape will be attacted with the report |  |  | Rejected | Not enough detail in comment, please clarify | No change | No change | No change
5.3104.2f | Single-Family Homes | Heating and Cooling | Hydronic Heating (Hot Water and Steam) | Equipment Maintenance, Testing, and Repair | Maintenance: Gas Boiler Service Inspection | Flue gas testing | Undiluted flue gases will be checked with a calibrated combustion analyzer in accordance with BPI BPI Building Performance Institute, www.bpi.org -1100-T-2012If combustion is not in compliance with BPI BPI Building Performance Institute, www.bpi.org -1100-T-2012, diagnostics and adjustments will be done to meet manufacturer specifications or local codes | Confirm that combustion occurs safely with maximum efficiency | Adjudicated - Redline only | 2013-04-01 | 2014-07-14 | Thom Knoll | At 5.3104.2f Flue Gas Testing, references compliance with BPI-1100-T-2012, but the referenced Home Energy Audit Standard does not seem to have any description or limit for undiluted flue gas content (or whatever else was supposed to be at this reference). | n/a |  | Accepted with modification | Spec will now refer to BPI 1200 | No change | Undiluted flue gases will be checked with a calibrated combustion analyzer in accordance with BPI 1200 or other approved standard If combustion is not in compliance with the referenced standard, diagnostics and adjustments will be referred to a qualified technician to meet manufacturer specifications or local codes | No change
6.6004.2g | Multifamily Homes | Ventilation | Exhaust | Exhaust Ventilation Systems | Individual Exhaust Fan Serving Multiple Rooms Within Single Dwelling Unit (All Building Types) | Backdraft dampers (required in intermittent systems) | A backdraft damper Backdraft damper A damper that allows air to flow in only one direction will be installed between the fan and the exterior unless the system operates continuously A backdraft damper Backdraft damper A damper that allows air to flow in only one direction will be installed in any duct serving any room with a separate exhaust (e.g., dryer) | Prevent reverse air flow when the system is offPrevent spread of contaminants between rooms | Adjudicated - Redline only | 2014-09-08 | 2014-09-08 | Steve Divan | Any ASHRAE fan is required to allow the occupant to be able to disable the fan. Even if a fan is intended to be used continuously, if it can be turned off then isn't a damper needed to prevent infiltration/exfiltration? | A Backdraft damper will be installed between the fan and the exterior. | No. ll fans I am aware of come with backdraft dampers, there should be no increase in cost. | Accepted | Clarifies SWS and achieves stated objective. | No change | A backdraft damper will be installed between the fan and the exterior A backdraft damper will be installed in any duct serving any room with a separate exhaust (e.g., dryer) | No change
6.6102.3a | Single-Family Homes | Ventilation | Supply | Components | Intake for Ventilation Air to Forced Air System Used for Heating or Cooling | Forced air system requirements | Existing forced air system leakage to outside will be less than 10% of the air handler flow when measured at 25 pascals with reference to outsideAny portion of the return located inside the combustion applianceZone will be air sealed | Reduce migration of pollutants | Adjudicated - Redline only | 2014-12-18 | 2014-12-18 | Kelly Cutchin C... | It appears this is an unfinished sentence. Not sure what is meant. | Clarify what is meant by second bullet item: Any portion of the return located inside the combustion appliance | No. | Accepted | Clarifies SWS and achieves stated objective. | No change | Existing forced air system leakage to outside will be less than 10% of the air handler flow when measured at 25 pascals with reference to outside Any portion of the return located inside the combustion appliance zone will be air sealed | No change
6.6201.1a | Single-Family Homes | Ventilation | Whole Building Ventilation | Air Flow Requirements | Installed System Air Flow | Separate exhaust for all baths and kitchens plus primary ventilation | Air flows will be measured and adjusted to meet the current version of ASHRAE ASHRAE American Society of Heating, Refrigerating and Air-Conditioning Engineers, www.ashrae.org 62.2 and in compliance with the authority having jurisdiction. See Calculation of the Infiltration Credit for calculation information and examples | Provide sufficient flows in accordance with current ventilation standards | Adjudicated - Redline only | 2014-04-23 | 2014-04-23 | Darrel Tenter Tenter | Insert space or line return before "For intermittent..." in last sentence. |  |  | Rejected | Language no longer in SWS | No change | No change | No change
6.6201.1a | Single-Family Homes | Ventilation | Whole Building Ventilation | Air Flow Requirements | Installed System Air Flow | Separate exhaust for all baths and kitchens plus primary ventilation | Air flows will be measured and adjusted to meet the current version of ASHRAE 62.2 and in compliance with the authority having jurisdiction. See Calculation of the Infiltration Credit for calculation information and examples | Provide sufficient flows in accordance with current ventilation standards | Adjudicated - Redline only | 2014-12-18 | 2014-12-18 | Kelly Cutchin C... | The language here is repeated in next row. Remove this row. | NA - remove this row, as it is repetitive with next row of this detail. | No. | Accepted with modification | Rewritten by committee and merged with Detail 6.6204.4 MH; Detail number 6.6202.1 will be deleted | Delete | Delete | Delete
6.6201.1b | Single-Family Homes | Ventilation | Whole Building Ventilation | Air Flow Requirements | Installed System Air Flow | Separate exhaust for all baths and kitchens sufficient to meet primary ventilation requirements | Air flows will be measured and adjusted to meet the current version of ASHRAE 62.2 and in compliance with the authority having jurisdiction. See Calculation of the Infiltration Credit for calculation information and examples | Provide sufficient flows per current ventilation standards | Adjudicated - Redline only | [6 empty] | Accepted with modification | Rewritten by committee and merged with Detail 6.6204.4 MH; Detail number 6.6202.1 will be deleted | Delete | Delete | Delete
6.6201.1c | Single-Family Homes | Ventilation | Whole Building Ventilation | Air Flow Requirements | Installed System Air Flow | Single additional fan to meet all ventilation requirements | Air flows will be measured and adjusted to meet the current version of ASHRAE 62.2 and in compliance with the authority having jurisdiction. See Calculation of the Infiltration Credit for calculation information and examples | Provide sufficient flows in accordance with current ventilation standards | Adjudicated - Redline only | [6 empty] | Accepted with modification | Rewritten by committee and merged with Detail 6.6204.4 MH; Detail number 6.6202.1 will be deleted | Delete | Delete | Delete
6.6202.3b | Multifamily Homes | Ventilation | Whole Building Ventilation | Components | Airflow Control Devices (All Building Types) | Preparation | Duct cleaning will be performed in compliance with ANSI ANSI American National Standards Institute, www.ansi.org / ACCA ACCA Air Conditioning Contractors of America, www.acca.org 6 HVAC HVAC Heating, ventilation, and air conditioning System Cleanliness-2007Register cleaning or replacement will be performed as specifiedDuct sealing will be performed as specifiedStack pressures will be verified for proper operation of flow control devicePresence and type of dampers and smoke control devices will be identified, and installer will ensure the installation of the air flow device will not interfere with proper operation | Establish preconditions for installing flow control deviceEnsure health and safety of occupant | Adjudicated - Redline only | 2014-12-03 | 2014-12-03 | Jim Harmon Harmon | Obviously duct cleaning is not required for all whole-building ventilation systems encountered by home performance/ Wx/ HVAC professionals. However, this spec could be misinterpreted as requiring duct cleaning as a preparation for all buildings/ systems. Please clarify verbiage. | Duct cleaning, when performed, will be performed in compliance with ANSI / ACCA 6 HVAC System Cleanliness-2007 | No; to the contrary. | Accepted | Clarifies SWS and achieves stated objective. | No change | Duct cleaning, when performed, will be performed in compliance with ANSI / ACCA 6 HVAC System Cleanliness-2007 Register cleaning or replacement will be performed as specified Duct sealing will be performed as specified Stack pressures will be verified for proper operation of flow control device Presence and type of dampers and smoke control devices will be identified, and installer will ensure the installation of the air flow device will not interfere with proper operation | No change
6.6202.9b | Multifamily Homes | Ventilation | Whole Building Ventilation | Components | Filtration for Fan-Powered (Active) Systems | Selection | All mechanically supplied outdoor air will pass through filter before conditioningFilters and filter racks/holders will have a rating of minimum efficiency rating value 6 or higher when tested in accordance with ASHRAE ASHRAE American Society of Heating, Refrigerating and Air-Conditioning Engineers, www.ashrae.org 52.2-2007Pressure drop across filter will match equipment capabilitiesFilter systems that produce ozone will not be allowed | Ensure outdoor air is filtered before entering occupied spaceEnsure occupant health and safety | Adjudicated - Redline only | 2014-04-22 | 2014-04-22 | Steve Divan | This should be included under single family and manufactured homes also. Systems that supply outside air can also be installed in those types of .housing |  |  | Accepted with modification | Add entire detail (6.6202.9) to SF and MH library. Remove year from 52.2 standard | No change | All mechanically supplied outdoor air will pass through filter before conditioningFilters and filter racks/holders will have a rating of minimum efficiency rating value 6 or higher when tested in accordance with ASHRAE 52.2 Pressure drop across filter will match equipment capabilities Filter systems that produce ozone will not be allowed | No change
6.6202.9b | Multifamily Homes | Ventilation | Whole Building Ventilation | Components | Filtration for Fan-Powered (Active) Systems | Selection | All mechanically supplied outdoor air will pass through filter before conditioningFilters and filter racks/holders will have a rating of minimum efficiency rating value 6 or higher when tested in accordance with ASHRAE ASHRAE American Society of Heating, Refrigerating and Air-Conditioning Engineers, www.ashrae.org 52.2-2007Pressure drop across filter will match equipment capabilitiesFilter systems that produce ozone will not be allowed | Ensure outdoor air is filtered before entering occupied spaceEnsure occupant health and safety | Adjudicated - Redline only | 2014-04-27 | 2014-04-27 | Steve Divan | It seems that this could apply to single family homes also. An HRV or ERV is occasionally installed in a single family home. I would think the filtration requirement would apply in those cases. |  |  | Accepted | Add entire detail (6.6202.9) to SF and MH library | No change | No Change | No change
6.6204.1a | Manufactured Housing | Ventilation | Whole Building Ventilation | Equipment Evaluation | Commissioning Existing Exhaust or Supply Ventilation Systems | Systems check | Visual inspection will be performed and documented for: Electrical connections Name plate (rated sone and flow) Damper operation (internal and external) Motor cleanlinessDucts: Connections (proper materials, sealed and connected) Insulation Support Sizing Termination | Evaluate systems | Adjudicated - Redline only | 2016-07-26 | 2016-07-26 | Charles Kurnik | Under committee guidance, The Detail 6.6204.1 is being rewritten to apply to single family and manufactured housing. 6.6201.1 is being deleted and incorporated into this rewrite. | Text to come. |  | Accepted | Language and changes proposed by committee: • Change Subtopic to "System Evaluation" • Change Detail name to "Commisioning Ventilation System" • Add detail to single-family homes in addition to manufactured housing | Identification | Identify whole building ventilation strategy that was installed in the home, based on options described in current version of ASHRAE 62.2, e.g., exhaust only, supply only, balanced, combining local and whole home ventilation delivery, incorporating infiltration credit, etc. | Ensure suitable whole building ventilation strategy is installed Identify testing requirements to determine installed system air flow
6.6204.1b | Manufactured Housing | Ventilation | Whole Building Ventilation | Equipment Evaluation | Commissioning Existing Exhaust or Supply Ventilation Systems | Verify flow rate | Calibrated device will be used to test for flow measurement | Ensure proper flow | Adjudicated - Redline only | N/A | N/A | N/A | N/A | N/A | N/A | Accepted | Language and changes proposed by committee: • Change Subtopic to "System Evaluation" • Change Detail name to "Commisioning Ventilation System" • Add detail to single-family homes in addition to manufactured housing | Equipment inspection | Visually inspect and document status of: · Electrical connections · Name plate (rated sone and flow) · Motor cleanliness | Evaluate equipment
6.6204.1c | Manufactured Housing | Ventilation | Whole Building Ventilation | Equipment Evaluation | Commissioning Existing Exhaust or Supply Ventilation Systems | Work order | Work order will be developed as necessary in accordance with systems check and flow rate | Correct deficiencies Ensure proper operation | Adjudicated - Redline only | N/A | N/A | N/A | N/A | N/A | N/A | Accepted | Language and changes proposed by committee: • Change Subtopic to "System Evaluation" • Change Detail name to "Commisioning Ventilation System" • Add detail to single-family homes in addition to manufactured housing | Pathway inspection | Visually inspect and document status of ducting or other airflow pathways to ensure proper: · Connections (proper materials, sealed and connected) · Insulation · Support · Sizing, and · Termination locations and fittings Verify proper damper operation | Preserve integrity of building envelope Effectively move air along selected pathways
6.6204.1d | Manufactured Housing | Ventilation | Whole Building Ventilation | Equipment Evaluation | Commissioning Existing Exhaust or Supply Ventilation Systems | Total ventilation airflow | Total exhaust and/or supply system ventilation airflow will be measured | Ensure airflow is as designed | Adjudicated - Redline only | N/A | N/A | N/A | N/A | N/A | N/A | Accepted | Language and changes proposed by committee: • Change Subtopic to "System Evaluation" • Change Detail name to "Commisioning Ventilation System" • Add detail to single-family homes in addition to manufactured housing | Measurement and Adjustment | Using a calibrated device, measure air flow of all necessary components, including building air leakage when relevant Adjust ventilation equipment air flows as necessary to meet the ventilation rates required by the current version of ASHRAE 62.2. | Provide sufficient air flows per current ventilation standards Verify suitable performance of installed ventilation strategy
6.6204.1e | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Adjudicated - Redline only | N/A | N/A | N/A | N/A | N/A | N/A | Accepted | New Spec Language and changes proposed by committee: • Change Subtopic to "System Evaluation" • Change Detail name to "Commisioning Ventilation System" • Add detail to single-family homes in addition to manufactured housing | Work order | Develop work order as necessary to correct deficiencies identified during inspections and measurement. | Correct deficiencies Ensure proper operation
6.6204.1f | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Adjudicated - Redline only | N/A | N/A | N/A | N/A | N/A | N/A | Accepted | New Spec Language and changes proposed by committee: • Change Subtopic to "System Evaluation" • Change Detail name to "Commisioning Ventilation System" • Add detail to single-family homes in addition to manufactured housing | Occupant education | Instruct occupant on purpose, use and maintenance of ventilation, and typical signs that ventilation is needed, e.g., condensation on windows. | Occupant understands benefits of good indoor air quality and can operate ventilation equipment as needed.
6.6205.1c | Manufactured Housing | Ventilation | Whole Building Ventilation | Exhaust-Only System | Manufactured Housing Exhaust-Only Strategies | Location | No resistance greater than 3 pascals will exist between fan intake location with reference to the common areaExhaust ventilation for common spaces will not be installed in bathrooms or bedrooms | Ensure fresh air distribution to common areas | Adjudicated - Redline only | 2014-04-22 | 2014-04-22 | Steve Divan | The comment that exhaust ventilation for common spaces will not be installed in bathrooms or bedrooms does not make sense. Why can't a whole house fan in a mobile home be located in a bathroom? This goes against what is allowed in the ASHRAE standard. |  |  | Accepted | Clarifies SWS and achieves stated objective. | No change | No resistance greater than 3 pascals will exist between fan intake location with reference to the common area | No change
6.6288.1b | Single-Family Homes | Ventilation | Whole Building Ventilation | Special Considerations | Sound-Rating Limits | Intermittent local ventilation system | Local ventilation will be rated for sound at a maximum of 3 sone, unless their maximum rated airflow exceeds 400 cfm CFM Cubic feet per minute , in accordance with ASHRAE ASHRAE American Society of Heating, Refrigerating and Air-Conditioning Engineers, www.ashrae.org 62.2-2010 | Minimize noise | Adjudicated - Redline only | 2015-06-12 | 2015-06-12 | Kelly Cutchin C... | Bring into alignment with other references to 62.2 and avoid maintenance issue of updating document every time a new ASHRAE 62.2 is published. | Local ventilation will be rated for sound at a maximum of 3 sone, unless their maximum rated airflow exceeds 400 cfm, in accordance with current ASHRAE 62.2 standard | No. | Accepted | Brought into line with item 6.6288.1a text. | No change | Local ventilation will be rated for sound at a maximum of 3 sone, unless their maximum rated airflow exceeds 400 cfm, in accordance with current ASHRAE 62.2 standard | No change
7.8003.1a | Single-Family Homes | Baseload | Plug Load | Lighting | Lighting Upgrade | Day lighting | Window coverings (e.g., blinds, shades, moveable insulation) will be replaced or maneuvered to maximize useful daylight where appropriateActive and passive day lighting will be properly oriented, designed, and installed where appropriate | Reduce energy use without negative consequences (e.g., glare, unintentional heating) | Adjudicated - Redline only | 2014-04-23 | 2014-04-23 | Darrel Tenter Tenter | Moveable is misspelled. Should be movable. |  |  | Accepted | Clarifies SWS and achieves stated objective. | No change | Window coverings (e.g., blinds, shades, movable insulation) will be replaced or maneuvered to maximize useful daylight where appropriateActive and passive day lighting will be properly oriented, designed, and installed where appropriate | No change
7.8102.2i | Single-Family Homes | Baseload | Water Heating | Installation and Replacement | Storage-Type Appliance | Thermal efficiency | If additional tank insulation is installed, it will be rated a minimum of R-11 and will be installed to manufacturer specificationsIf additional insulation is installed, it will be installed based on fuel type, making sure not to obstruct draft diverter, pressure relief valve, thermostats, hi-limit switch Hi-limit switch A protective electronic switch that keeps a burner from continuing to operate and damage the appliance , plumbing pipes or elements, and thermostat access platesThe first 6' of inlet and outlet piping will be insulated in accordance with manufacturer specificationsPipe insulation must remain 3'' from gas water heater ventHeat traps will be installed on the inlet and outlet piping where not provided by manufacturer | Reduce standby loss Standby loss Heat loss through the outer part of a water heater. Energy that is used even when a device is turned off from near tank piping and storage tankEnsure insulation does not make contact with flue gas venting | Adjudicated - Redline only | 2015-02-17 | 2015-02-17 | Ken Feller | The minimum distance of 3" to pipe insulation to vent stated here is at least confusing and at worst in conflict with NFPA 211 and the 2012 IRC, Table G2427.10.5. The term "vent" in the IRC is defined as a manufactured device such as "B" vent that uses a clearance specified by the manufacturer. Most often in the field, the clearance issue with pipe insulation is to a "connector" as defined by IRC usually single wall pipe, which in the table cited requires a minimum clearance of 6". Please clarify. | Combustible pipe insulation must maintain a minimum clearance of 6" from gas water heater draft hood andor single wall metal pipe. Clearance from vent such as "B" vent should be maintained per vent manufacturer's specifications. | No. | Accepted with modification | Clarifies SWS and achieves stated objective, made same edits to manufactured housing. | No change | If additional tank insulation is installed, it will be rated a minimum of R-11 and will be installed to manufacturer specifications If additional insulation is installed, it will be installed based on fuel type, making sure not to obstruct draft diverter, pressure relief valve, thermostats, hi-limit switch, plumbing pipes or elements, and thermostat access plates The first 6' of inlet and outlet piping will be insulated in accordance with manufacturer specifications Combustible pipe insulation must maintain a minimum clearance of 6" from gas water heater draft hood and/or single wall metal pipe. Clearance from vent such as "B" vent should be maintained per vent manufacturer's specifications Heat traps will be installed on the inlet and outlet piping where not provided by manufacturer | No change
7.8104.3d | Multifamily Homes | Baseload | Water Heating | Distribution | Piping | Insulation | All piping and fittings will be insulated with fixed insulation to IECC IECC International Energy Conservation Code 2012 or ASHRAE ASHRAE American Society of Heating, Refrigerating and Air-Conditioning Engineers, www.ashrae.org 90.1-2010, at a minimumTanks will be insulated to a minimum of R-12.5Insulation will be protected from damage (e.g., protected from underground water, contact, friction from pipe hangers, woodpeckers, ultraviolet radiation ) | Prevent the pipe from freezingMinimize heat loss from the pipesReduce the risk of moisture damage | Adjudicated - Redline only | 2015-04-22 | 2015-04-22 | Kelly Cutchin C... | N/A | You can delete this comment after reading. Just wanted to point out that we're protecting the insulation from many things, including, specifically, woodpeckers. I wish I'd been on this committee! | No. | Rejected | Rejected per commenter instructions | No change | No change | No change
Note on N64: kelly: less about the technical validity; SWS should be used as if/then, they are not prescriptive measures for EVERYONE to ALWAYS follow
Note on A79: Alison Holm: Classification originally listed as 4.1005.3c. Updated to 4.1005.3e to reflect comments.
Note on N80: NREL: Are there standards for open, medium, dense pack?
Note on N102: NREL: class A is 0-25 flame spread

## Sheet2 (hidden)
Accepted
Accepted with Modifications
Further Investigation Required
Rejected