## 2017 Comment Spreadsheet
Classification | Housing Type | Section | Topic | Subtopic | Detail | Title | Existing specification | Objective language | Status | Submitted | Updated | Submitted By | Comment | Justification/substantiation | Cost increase | Committee Adjudication (drop down list) | Committee Rationale for Decision | Proposed Spec number change | Proposed Title | Proposed Specification(s) | Proposed Objective(s)
2.0100.1a | Single-Family Homes | Health and Safety | Safe Work Practices | Safe Work Practices | Global Worker Safety | Prevention through design | Design will be incorporated to eliminate or minimize hazards (e.g., material selection, access to equipment for installation and maintenance, placement of equipment, ductwork and condensate lines) | Prevent worker injuriesReduce risk exposure to toxic substances and physical hazards | Not Yet Reviewed | 2016-02-05 | 2016-02-05 | Jonathan Coulter | Currently, 1) 2.0100.1, 2.0100.2 and 2.0100.3 have similar, but incomplete information located in three different SWSs and 2) 2.0100.1, 2.0100.2 and 2.0100.3 have valuable prep/assessment/inspection information that doesn't align with the desired outcomes of these topics, but do align with 2.0100.4. | 1) All of the specifications in 2.0100.1, 2.0100.2 and 2.0100.3 should be aligned and consolidated into one Subtopic with three housing type tabs, "Single-Family Homes, Manufactured Housing, Multifamily Homes". 2) All specifications that relate to prep/assessment/inspection (e.g. 2.0100.1d electrical assessment, 2.0100.1g frayed electrical wires) should be relocated to 2.0100.4 to match the desired outcome for each SWS. | Again, this consolidation and alignment may save money by limiting the differences between the documents and reducing the variation for crews, field folders, trainings, etc. | Accepted with Modifications | Health and Safety Section was crosswalked across housing types such that the specfications will align with a separate tab for each housing type
2.0100.1a | Single-Family Homes | Health and Safety | Safe Work Practices | Safe Work Practices | Global Worker Safety | Prevention through design | Design will be incorporated to eliminate or minimize hazards (e.g., material selection, access to equipment for installation and maintenance, placement of equipment, ductwork and condensate lines) | Prevent worker injuriesReduce risk exposure to toxic substances and physical hazards | Not Yet Reviewed | 2016-08-09 | 2016-08-09 | Joel Harms | Ease of use is ample justification to permit filtering by housing type. | I am submitting a general question rather than a comment to a specific topic. Is there a way to filter the SWS by housing type? I would like to eliminate all of the topics, subtopics, details, etc. that pertain to manufactured housing and multi-family housing when I am only interested in single-family housing, or vice versa. I realize this filter is available in My Favorites, but I would have to add everything in the database to My Favorites to make the filter work? Seems this would be a relatively simple addition to the database and a very helpful one to the users to be able to sort out info from the top that is not applicable. Thanks. | No. | Accepted with Modifications | The SWS is a searchable webtool with the ability to filter search results by housing type. As noted in your comment, you can also add Details to your favorites. Unfortunately, the SWS is not able to remove housing types from its regular browsing view. We hope to add this functionality in the future. |  | NA | NA | NA
2.0100.4a | Multifamily Homes | Health and Safety | Safe Work Practices | Safe Work Practices | Work Area Inspection and Stabilization | Inspect to confirm integrity of existing building assembly | An inspection will be conducted for existing conditions that may hinder successful installation of proposed energy improvement | Ensure the work area and associated building assemblies are suitable for the proposed work | Not Yet Reviewed | 2016-02-05 | 2016-02-05 | Jonathan Coulter | The specification in this Subtopic are applicable to manufactured housing and single-family homes inspection/prep/assessments. And currently language around inspection/prep/assessments is buried in "work completed" subtopics by housing type. Therefore, I'm suggestion to align and streamline entire Subtopic to be more user friendly. | This specification and all related to 2.0100.4 also have a connection and influence with Manufactured Housing and Single-Family Homes. Therefore, I propose two parts: 1)add "Manufactured Housing" and "Single-Family Homes" tabs to the top of this format (like 2.0103.1), and 2)align all other prep/assessment language from all 2.0100 Subtopics with this "work area inspection and stabilization" topic. | This may actually lower the cost by reducing the amount of time someone sifts through related information that is currently separated, unnecessarily by housing type. | Accepted with Modifications | Health and Safety Section was crosswalked across housing types such that the specfications will align with a separate tab for each housing type
2.0105.4h | Manufactured Housing | Health and Safety | Safe Work Practices | Heating and Cooling Equipment | Heating and Cooling Worker Safety | Safety devices | A secondary LP safety detector system (valve, exhaust fan, alarm light) will be installed by a certified professional for propane piping installed below grade Shut off valves will be installed by a certified professional at each gas appliance ( ANSI ANSI American National Standards Institute, www.ansi.org Z21.15) | Detect accumulation of dangerous levels of propane in below-grade areas Isolate appliances from the rest of the system for emergencies, removal, or repairs | Not Yet Reviewed | 2017-01-20 | 2017-01-20 | Kelly Cutchin C... | This does not fit into the overall SWS objective of worker safety. If the worker is not installing new equipment, it seems to be overkill to add safety detector systems and shut off valves to existing piping. | ADD "When installing new equipment..." before both parts of the specification. | No. | Accepted with Modifications | Clarifies SWS. New equipment installation was removed because it does not fit within the health and safety section and shut off valves are already required by code. |  | Delete row | Delete row | Delete row
2.0201.1a | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Assessment | Emergency problems (e.g., gas leak, ambient CO CO Carbon monoxide levels that exceed 35 ppm) will be communicated clearly and immediately to the customer and appropriate solutions will be suggestedDetermine if combustion and dilution air is adequate for proper combustion and venting of all equipment within the CAZ CAZ Combustion appliance zone Examine appliance for signs of damage, misuse, improper repairs, and lack of maintenance | Ensure system does not have fatal problemsEnsure combustion appliance has adequate combustion and dilution air | Not Yet Reviewed | 2017-01-13 | 2017-01-13 | State of Alaska... | current deferral policies deals with this | In response to redline document changes, agencies should not be required to contact emergency services, the client should contact emergency services, The job should be deferred until the situation is corrected following subgranteee approved process. | no | Accepted with Modifications | Current redline document not clear on who is responsible to contact emergency services. We don't want to relie on the customer to contact appropriate personnel. We clarified ambient instead of the gas leak and broadened the acceptable personnel that should be contacted. |  | No change. | Emergency problems (e.g., ambient gas levels greater than 10% Lower Explosion Limit (LEL), ambient CO levels that exceed 70 ppm) will be communicated clearly and immediately to the customer, the home shall be evacuated, and appropriate personnel (e.g.: HVAC technician, utility, emergency services) shall be contacted. Significant problems (e.g., gas leak less than 10% LEL, ambient CO levels that exceed 35 ppm but less than 70 ppm) will be communicated clearly and immediately to the customer and appropriate solutions will be suggested Examine appliance for signs of damage, misuse, improper repairs, and lack of maintenance | Ensure system does not have potentially fatal problems
2.0201.1a | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Assessment | Emergency problems (e.g., gas leak, ambient CO CO Carbon monoxide levels that exceed 35 ppm) will be communicated clearly and immediately to the customer and appropriate solutions will be suggestedDetermine if combustion and dilution air is adequate for proper combustion and venting of all equipment within the CAZ CAZ Combustion appliance zone Examine appliance for signs of damage, misuse, improper repairs, and lack of maintenance | Ensure system does not have fatal problemsEnsure combustion appliance has adequate combustion and dilution air | Not Yet Reviewed | 2017-01-18 | 2017-01-18 | Jonathan Ballew | Conforming to BPI 1200 will do little to make the program better but will create a need to purchase a lot of equipment throughout the network. | The 2016 SWS update should eliminate the mention of measuring LEL. This will require the unnecessary purchase and therefore financial burden of replacing gas sniffers that are still operational in favor of those with a digital display. | no, keeping the gas leak testing procedure the way that it is will eliminate the need for contractors to replace gas sniffers that are doing an adequate job. | Rejected | Keep redline with changes accepted wording to remain consistent with BPI 1200. Compliance with OSHA confined spaces will also require this equipment.
2.0201.1c | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Venting | For oil systems, the presence and operability of a draft regulator will be verified and tested Combustion venting systems will be inspected for damage, leaks, disconnections, inadequate slope, and other safety hazards | Determine if a draft regulator Draft regulator A device that functions to maintain a desired draft in the appliance by automatically reducing the draft to the desired value. Source: National Fire Protection Association 54, 2012 is present and working and if vent system is in good condition and installed properly | Not Yet Reviewed | 2017-01-13 | 2017-01-13 | State of Alaska... | We need to remember this is a minimum set of standards. | In reference too the redline document, not all oil heating require a draft regulator. The original language was to determine if there was a draft regulator present and in working order. This seems like a sufficient minimum standard. | The proposed redline change would require more technical expertise, this could add cost. | Accepted with Modifications | Modified redline language for clarity |  | No change. | For oil systems that require a draft regulator, the presence and operability of it (that draft regulator) will be verified and tested Combustion venting systems will be inspected for damage, leaks, disconnections, inadequate slope, and other safety hazards | Determine if a regulator is present and working Determine whether vent system is in good condition and installed properly
2.0201.1d | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Base pressure test | Baseline pressure will be measured in Combustion Appliance Zone with reference to outdoors | Measure pressure difference between combustion zone and the outside under natural conditions | Not Yet Reviewed | 2017-01-20 | 2017-01-20 | Kelly Cutchin C... | No need for this test when direct or power vented equipment is present. | Baseline pressure will be measured in Combustion Appliance Zone with reference to outdoors where natural draft equipment is present. | No | Accepted | Clarifies language |  | No change. | When atmospherically vented appliances are located inside the pressure boundary, baseline pressure will be measured in Combustion Appliance Zone with reference to outdoors. | No change.
2.0201.1e | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test | Depressurization test will include exhaust fans, interior door closure, or duct leakage, or a combination thereof, and will not be more negative than -3 pascals accounting for base pressure | Measure combined effect of mechanical system fans on combustion zone | Not Yet Reviewed | 2017-01-18 | 2017-01-18 | Jonathan Ballew | This clarifies the scope of the appliances being tested. I think of a draft diverter and a draft hood as two different things with the same function. I think of a draft diverter as a part of a combustion water heaters venting system, whereas a draft diverter is found on a furnace. The way that this is worded makes it sound like only water heaters apply to this standard. | CAZ depressurization testing will be administered for all equipment equipped with a draft hood/draft diverter. Add draft diverter to the 2016 proposed change. | no. | Accepted with Modifications | Broaden the terminology options for the nation. But we need to align with BPI Standard 1200, modified existing redline language. |  | No change | CAZ depressurization testing will be administered for all atmospherically vented appliances located inside the pressure boundary. Depressurization test will include exhaust fans, interior door closure, or duct leakage, or a combination thereof; the test will be done to determine the largest negative pressure per BPI Standard 1200. | Determine worst-case depressurization in combustion zone due mechanical system fans
2.0201.1g | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Carbon monoxide ( CO CO Carbon monoxide ) test in appliance vent | CO CO Carbon monoxide will be tested for in undiluted flue gases of combustion appliancesIf CO CO Carbon monoxide levels exceed 200 ppm as measured, or 400 ppm air-free measurement, service will be provided to reduce CO CO Carbon monoxide to below these levels (unless CO CO Carbon monoxide measurement is within manufacturer specifications)If the outlet of the exhaust is accessible, include a CO CO Carbon monoxide test on all sealed-combustion, direct vent, and power-vented appliances (without atmospheric chimneys) | Measure CO CO Carbon monoxide and report excessive levels | Not Yet Reviewed | 2017-01-13 | 2017-01-13 | State of Alaska... | This doesn't provide an accurate reading. | In regard to redline doc, shouldn't be tested in worst case, but in normal condition. |  | Rejected | Disagree as the reference standard for this test protocol is BPI Stardard 1200 stating to test under greatest CAZ depressurization.
2.0201.3g | Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Carbon monoxide ( CO CO Carbon monoxide ) test in appliance vent | CO CO Carbon monoxide will be tested for in undiluted flue gases of combustion appliancesFor CO CO Carbon monoxide levels exceeding 100 ppm as measured or 200 ppm air-free measurement, service will be provided to reduce CO CO Carbon monoxide to below these levels (unless CO CO Carbon monoxide measurement is within manufacturer specifications)If the outlet of the exhaust is accessible, include a CO CO Carbon monoxide test on all sealed- combustion and power-vented appliances (without atmospheric chimneys) | Measure CO CO Carbon monoxide and report excessive levels | Not Yet Reviewed | 2016-12-09 | 2016-12-09 | Kelly Cutchin C... | All other combustion safety related numbers have been updated for consistency with BPI 1200, this must have slipped through. | Update CO action levels to 200 ppm as measured and 400 ppm air-free to match BPI 1200 and similar single-family SWS | No | Accepted | Merged entire detail (2.0201.3) with detail 2.0201.1 in order to consolidate housing types |  | No change | No change | No change
2.0203.1a | Single-Family Homes | Health and Safety | Combustion Safety | Vented Gas Appliances | Combustion Air for Natural Draft Appliances | Required combustion air | The required volume of indoor air will be determined in accordance with 2012 IRC IRC International Residential Code Section G2407.5.1 or G2407.5.2 and authority having jurisdiction, except that where the air infiltration Infiltration The uncontrolled passage of outside air into a building through unintended leaks in the building envelope rate is known to be less than 0.40 air changes per hour (ACH), 2012 IRC IRC International Residential Code Section G2407.5.2 will be used | Determine if existing conditions meet the combustion air calculation | Not Yet Reviewed | 2017-01-25 | 2017-01-25 | Kelly Cutchin C... | We must ask ourselves why we conduct all these depressurization and spillage tests if we don't trust the results. Can the results be used to determine there is adequate combustion air, at least when we are talking about existing equipment? | For this and next row, consider allowing performance testing be used to determine if there is a problem, as an option. | No. | Accepted | Clarifies language, Spec 2.0203.1b was previously changed in the 2016 Redline |  | No change | The required volume of indoor air will be determined in accordance with 2012 IRC Section G2407.5.1 or G2407.5.2 and authority having jurisdiction, except that where the air infiltration rate is known to be less than 0.40 air changes per hour (ACH), 2012 IRC Section G2407.5.2 will be used Exception: Existing appliances that have passed combustion safety testing per BPI 1200 are deemed to have sufficient combustion air | No change
2.0203.2d | Single-Family Homes | Health and Safety | Combustion Safety | Vented Gas Appliances | Combustion Flue Gas&mdash;Orphaned Water Heaters | Required combustion air | The minimum required volume will be 50 cubic feet per 1,000 Btu BTU British thermal unit /h in accordance with 2012 IRC IRC International Residential Code G2407.5.1 and authority having jurisdiction | Determine if existing conditions meet the combustion air calculation | Not Yet Reviewed | 2017-01-25 | 2017-01-25 | Kelly Cutchin C... | Mentioned in previous comments. | Consider allowing results of performance based testing as an option to determine if additional combustion air is needed. | No. | Accepted | Clarifies SWS. |  | No Change | The minimum required volume will be 50 cubic feet per 1,000 Btu /h in accordance with 2012 IRC G2407.5.1 and authority having jurisdiction. Exception: Existing appliances that have passed combustion safety testing per BPI 1200 are deemed to have sufficient combustion air. | No change
2.0203.2d | Single-Family Homes | Health and Safety | Combustion Safety | Vented Gas Appliances | Combustion Flue Gas&mdash;Orphaned Water Heaters | Required combustion air | The minimum required volume will be 50 cubic feet per 1,000 Btu BTU British thermal unit /h in accordance with 2012 IRC IRC International Residential Code G2407.5.1 and authority having jurisdiction | Determine if existing conditions meet the combustion air calculation | Not Yet Reviewed | 2017-01-18 | 2017-01-18 | Jonathan Ballew | Calculating combustion air should be done as a response to spillage issues or if a new system is being installed. The testing procedure must not be used for determining if the system complies with the current version of code. We are specifically prohibited from bringing things up to code for the sake of bringing them up to code in WPN 11-6. This seems to contradict that. Same for 2.0203.7. Additionally, combustion air requirements are brought up in 2.0203.1. | 2.0203.2d should be eliminated | no | Accepted with Modifications | The language of the detail has been modified to allow performance testing to meet the requirement. But, if the appliance fails, it is appropriate to keep the detail. |  | No change | The minimum required volume will be 50 cubic feet per 1,000 Btu /h in accordance with 2012 IRC G2407.5.1 and authority having jurisdiction. Exception: Existing appliances that have passed combustion safety testing per BPI 1200 are deemed to have sufficient combustion air. | No change
2.0203.2e | Single-Family Homes | Health and Safety | Combustion Safety | Vented Gas Appliances | Combustion Flue Gas&mdash;Orphaned Water Heaters | Additional combustion air (if action is required) | Additional combustion air will be provided in accordance with 2012 IRC IRC International Residential Code G2407 or other authority having jurisdiction | Ensure adequate combustion air for operation of the appliance | Not Yet Reviewed | 2017-01-18 | 2017-01-18 | Jonathan Ballew | Calculating combustion air should be done as a response to spillage issues or if a new system is being installed. The testing procedure must not be used for determining if the system complies with the current version of code. We are specifically prohibited from bringing things up to code for the sake of bringing them up to code in WPN 11-6. This seems to contradict that. Same for 2.0203.7. Additionally, combustion air requirements are brought up in 2.0203.1. | eliminate 2.0203.2e | no. | Rejected | The situation has been addressed in response to the previous detail.
2.0203.4a | Manufactured Housing | Health and Safety | Combustion Safety | Vented Gas Appliances | Combustion Air for Natural Draft Appliances | Required combustion air | The required volume of indoor air will be determined in accordance with Section G2407.5.1 or G2407.5.2 and authority having jurisdiction, except where the air infiltration Infiltration The uncontrolled passage of outside air into a building through unintended leaks in the building envelope rate is known to be less than 0.40 air changes per hour (ACH), at which time Section G2407.5.2 will be used | Determine if existing conditions meet the combustion air calculation | Not Yet Reviewed | 2017-01-25 | 2017-01-25 | Kelly Cutchin C... | When dealing with an existing building, and existing equipment, if testing proves the system is functioning as it should, that should be allowed as an option. Otherwise, if we don't trust the results of those tests, what is the purpose? Please apply the suggested language for consideration in previous combustion air SWS comments, and to 2.0203.5c and any others I may have missed. | The required volume of indoor air will be determined either: through successful completion of performance based testing, (allowed only for existing appliances, add SWS references to applicable combustion safety SWS), or in accordance with Section G2407.5.1 or G2407.5.2 and authority having jurisdiction, except where the air infiltration rate is known to be less than 0.40 air changes per hour (ACH), at which time Section G2407.5.2 will be used | No. | Accepted with Modifications | Health and Safety Section was crosswalked across housing types such that the specfications will align with a separate tab for each housing type
2.0203.7a | Multifamily Homes | Health and Safety | Combustion Safety | Vented Gas Appliances | Combustion Air&mdash;Boilers | Combustion air | Combustion air shall be calculated and provided in conformance with the applicable code adopted by the jurisdiction and manufacturer requirements.In instances where conflicts occur between the code and the manufacturer's installation instructions, the more restrictive provisions shall apply (i.e., more air rather than less)In absence of a local code, combustion air shall be calculated and provided in conformance with any of the following: NFPA NFPA National Fire Protection Association, www.nfpa.org 54, IFGC IFGC International Fuel Gas Code , or NFPA NFPA National Fire Protection Association, www.nfpa.org 31 | Meet burner combustion air requirements | Not Yet Reviewed | 2017-01-18 | 2017-01-18 | Jonathan Ballew | Calculating combustion air should be done as a response to spillage issues or if a new system is being installed. The testing procedure must not be used for determining if the system complies with the current version of code. We are specifically prohibited from bringing things up to code for the sake of bringing them up to code in WPN 11-6. This seems to contradict that. Same for 2.0203.7. Additionally, combustion air requirements are brought up in 2.0203.1. | 2.0203.7 should be eliminated. | no. | Accepted with Modifications | The language of the detail has been modified to allow performance testing to meet the requirement. But, if the appliance fails, it is appropriate to keep the detail. |  | No Change | Combustion air shall be calculated and provided in conformance with the applicable code adopted by the jurisdiction and manufacturer requirements In instances where conflicts occur between the code and the manufacturer's installation instructions, the more restrictive provisions shall apply (i.e., more air rather than less) In absence of a local code, combustion air shall be calculated and provided in conformance with any of the following: NFPA 54, IFGC, or NFPA 31. Exception: Existing appliances that have passed combustion safety testing using the procedures of BPI 1200 are deemed to have sufficient combustion air. | No changes
2.0299.1a | Single-Family Homes | Health and Safety | Combustion Safety | Additional Resources | Combustion Appliance Depressurization Limits Table | Atmospheric water heater only (Category I, natural draft), open-combustion appliances | Manufacturer's certified negative pressure tolerance rating:Limit -2 pascals | Ensure appliances meet manufacturer's certified negative pressure tolerance rating | Not Yet Reviewed | 2015-10-29 | 2015-10-29 | John Cain | Directly from the BPI Building Analyst Professional Standard. | Specifications: Manufacturer's certified negative pressure tolerance rating: Limit -5 pascals | No | Rejected | The entire detail has been deleted.
2.0299.1a | Single-Family Homes | Health and Safety | Combustion Safety | Additional Resources | Combustion Appliance Depressurization Limits Table | Atmospheric water heater only (Category I, natural draft), open-combustion appliances | Manufacturer's certified negative pressure tolerance rating:Limit -2 pascals | Ensure appliances meet manufacturer's certified negative pressure tolerance rating | Not Yet Reviewed | 2015-10-29 | 2015-10-29 | John Cain | taken directly from BPI Building Analyst Professional | TITLE: Orphaned natural draft water heater (including outside chimneys) | No | Rejected | The entire detail has been deleted.
2.0301.1a | Single-Family Homes | Health and Safety | Safety Devices | Combustion Safety Devices | Smoke Alarm | Smoke alarm (hardwired) | Smoke alarms will be listed and labeled in accordance with UL UL Underwriters Laboratories 217 and installed (hardwired) in accordance with the 2012 IRC IRC International Residential Code or as required by the authority having jurisdiction | Ensure proper installation | Not Yet Reviewed | 2017-01-25 | 2017-01-25 | Kelly Cutchin C... | With the use of modern lithium batteries we can ensure the operation of smoke alarms for about 5 years, which is about the limit of the sensors. | This comment proposes a reorganization of this spec, for SF and MH. Currently we reference IRC 2012, which requires that hardwires smoke alarms be installed if an attic or crawlspace is available to run wiring. This is often above and beyond a reasonable scope of work in a weatherization retrofit. Suggest either separating out so hardwired and battery operated appear as completely separate SWS, OR combining them into one row that says existing smoke alarms will be tested for functionality, and if needed new ones will be installed that are either hard-wired in accordance with...(fill in references) or batter operated and meet minimum standards of...(fill in references). | No. | Accepted with Modifications | Clarifying that it is for hardwired smoke alarms. Please see the following spec that allows for battery operated smoke alarms. CK: After speaking with Kelly and Jonathan, we decided to create a seperate Detail for "Smoke Alarm - Battery Operated", and seperate Detail "Smoke Alarm - Hardwired". Do the same for Combustion alarms and monitors. |  | No Change | When installing hardwired smoke alarms, it will be listed and labeled in accordance with UL 217 and installed in accordance with the IRC or as required by the authority having jurisdiction | No change
2.0301.1b | Single-Family Homes | Health and Safety | Safety Devices | Combustion Safety Devices | Smoke Alarm | Smoke alarm (battery operated) | Battery operated alarms will be installed in accordance with the 2012 IRC IRC International Residential Code and manufacturer specifications | Ensure proper installation | Not Yet Reviewed | 2015-11-12 | 2015-11-12 | Kelly Cutchin C... | Current spec references 2012 IRC, but that allows battery operated alarms only when remodels do not remove interior finishes AND there is no access to wiring in attic or crawl space. I think intent of this SWS is to allow battery operated smoke alarms in basic energy upgrade scenarios where it doesn't really qualify as a remodel, so removing the IRC reference would help clarify. Ref. IRC sec. 314 | Suggest updating spec to: Battery operated alarms will be installed in accordance with manufacturer specifications | No. | Accepted with Modifications | Clarified when you are installing the alarm versus if the alarm is existing. Took out the IRC reference. |  | No Change | When installing battery operated smoke alarms, it will be installed in accordance with manufacturer specifications | No change
2.0301.1b | Single-Family Homes | Health and Safety | Safety Devices | Combustion Safety Devices | Smoke Alarm | Smoke alarm (battery operated) | Battery operated alarms will be installed in accordance with the 2012 IRC IRC International Residential Code and manufacturer specifications | Ensure proper installation | Not Yet Reviewed | 2015-11-16 | 2015-11-16 | Trent Williams | As it is written currently the SWS states battery operated alarms will be installed in accordance with 2012 IRC but when you reference 2012 IRC it specifies in section R314.4 Power Source: Smoke alarms shall receive their primary power from the building wiring when such wiring is served from a commercial source, and when primary power is interrupted, shall receive power from a battery. Wiring shall be permanent and without a disconnecting switch other than those required for overcurrent protection. Exceptions: 1. Smoke alarms shall be permitted to be battery operated when installed in buildings without commercial power. 2. Hard wiring of smoke alarms in existing areas shall not be required where the alterations or repairs do not result in the removal of interior wall or ceiling finishes exposing the structure, unless there is an attic, crawl space or basement available which could provide access for hard wiring without the removal of interior finishes. My interpretation of this, if I understand correctly is that if there is access to attic or crawlspace to run the wiring then the smoke detectors must be hardwired and battery operated would not be an option, and since almost every home that is weatherized has an attic or crawlspace then we would be required to hardwire all smoke detectors. I feel that this would be outrageously expensive and time consuming and detrimental to the weatherization program | Unsure of wording but some clarification needs to be given in reference to 2012 IRC specifically Section R-314.4 Power Source | Installing battery operated smoke detectors will be far less expensive and time consuming than hardwiring. | Accepted with Modifications | See above |  | No Change | When installing battery operated smoke alarms, it will be installed in accordance with manufacturer specifications | Ensure proper installation
2.0401.1a | Manufactured Housing | Health and Safety | Moisture | Air Sealing | Air Sealing Moisture Precautions | Moisture precautions for attics | Roof leaks will be repaired before performing attic air sealing or insulationMoisture sources in the house that can generate moisture into the attic will be identified and removed or reduced | Ensure durability of repairsReduce potential for occupant exposure to mold and other moisture-related hazardsPrevent moisture from communicating from within the conditioned space into unconditioned attic space when economically feasible | Not Yet Reviewed | 2017-01-18 | 2017-01-18 | Jonathan Ballew | The risk of vapor diffusion through and air tight attic assembly is next to none. Additionally, how would it be possible to install 2” of closed cell foam in a manufactured home attic? Air sealing the attic assembly is sufficient to limiting moisture migration into the attic space. | 2016 Redline change. 2.0401.1a (3) remove ‘water resistant’ provision. | no | Accepted with Modifications | We've addressed the issue with different language than proposed. Only addressed in Manufactured Housing. |  | No Change | Roof leaks will be repaired before performing attic air sealing or insulation Moisture sources in the house that can generate moisture into the attic will be identified and removed or reduced Where possible, water resistant sealants and/or closed cell foams will be used in cold climates. Plastic, foil, or any other Class 1 vapor barrier will not be used in hot humid climates In marine climates, vapor permeable materials will be used to block and seal penetrations in attic | Ensure durability of repairs Reduce potential for occupant exposure to mold and other moisture-related hazards Prevent moisture from communicating from within the conditioned space into unconditioned attic space. Increase durability of seal Avoid moisture-related damage to the home
2.0401.1b | Single-Family Homes | Health and Safety | Moisture | Air Sealing | Air Sealing Moisture Precautions | Moisture precautions for crawl spaces | Exposed earth will be covered with a continuous, durable, sealed Class 1 vapor retarder Vapor retarder A material that slows the passage of water vapor and contains a perm rating above 1 a minimum of 6 mils in thicknessPlastic, foil or any other Class 1 vapor barrier Vapor barrier A material that retards the passage of water vapor and contains a perm rating of less than 1 /retarder will not be used in hot-humid climatesAll accessible penetrations between the crawl space or basement and outside will be sealedHoles between the crawl space or basement and the living space will be sealed | Ensure durability of repairsReduce potential for occupant exposure to mold and other moisture-related hazards | Not Yet Reviewed | 2017-01-18 | 2017-01-18 | Jonathan Ballew | This is confusing and could be interpreted as a blanket statement that the living space should always be air sealed from the basement/crawlspace which generally speaking is not what the science would say. | eliminate "holes between the crawl space or basement and the living space will be sealed". | no. | Rejected | Basements have already been addressed in the redline version and holes between the crawl space and the living space should be sealed.
2.0402.1a | Single-Family Homes | Health and Safety | Moisture | Drainage | Crawl Spaces&mdash;Drainage | Exterior grading | Ground will be sloped away from the house at a rate of 6" of fall within 10' | Drain water away from the foundation wall | Not Yet Reviewed | 2017-01-25 | 2017-01-25 | Kelly Cutchin C... | In retrofit situations, if there is not problem, altering grading seems excessive. | In retrofit situations where there is evidence of previous moisture damage, or site assessment reveals the potential for such, ground will be sloped away from the house at a rate of 6" of fall within 10'. | No | Rejected | This is the expected outcome if you choose to use this measure.
2.0402.1b | Single-Family Homes | Health and Safety | Moisture | Drainage | Crawl Spaces&mdash;Drainage | Roof drainage | If downspouts are present (e.g., gutters, overhangs, French drain), they will be drained a minimum of 6' away from the house | Prevent roof water from leaking into the crawl space or basement | Not Yet Reviewed | 2017-01-25 | 2017-01-25 | Kelly Cutchin C... | overhangs and french drains are quite different from gutters and overhangs, in terms of downspouts. | In retrofit situations where there is evidence of previous moisture damage, or site assessment reveals the potential for such, if downspouts are present they will be drained a minimum of 6' away from the house | no | Rejected | This is the expected outcome if you choose to use this measure.
2.0402.1c | Single-Family Homes | Health and Safety | Moisture | Drainage | Crawl Spaces&mdash;Drainage | Exterior waterproofing | Foundation walls will be waterproof Exterior foundation drains will be installed | Prevent water from leaking into the crawl space or basement | Not Yet Reviewed | 2017-01-25 | 2017-01-25 | Kelly Cutchin C... | For a regular retrofit operation, this activity would be overly excessive if there were no evidence of a problem. | Add language suggested in 2.0402.1a regarding retrofits and only if problems are indicated. | no | Rejected | This is the expected outcome if you choose to use this measure.
2.0402.1d | Single-Family Homes | Health and Safety | Moisture | Drainage | Crawl Spaces&mdash;Drainage | Interior grading | Interior grading will be sloped to one or more collection points, if possible | Collect interior water for removal | Not Yet Reviewed | 2017-01-25 | 2017-01-25 | Kelly Cutchin C... | See previous comments. | Add text suggested in previous rows, to this and 2.0402.1e. The action should be taken only where necessary. Currently the SWS reads as if these actions are required in every crawl space. | no | Rejected | This is the expected outcome if you choose to use this measure.
2.0403.1b | Single-Family Homes | Health and Safety | Moisture | Vapor Barriers | Vented Crawl Spaces&mdash;Ground Moisture Barrier | Coverage | A ground moisture barrier that covers 100% of the exposed crawl space floor will be installed | Reduce ground moisture entering the crawl space | Not Yet Reviewed | 2017-01-25 | 2017-01-25 | Kelly Cutchin C... | If they can't access 100% of the area, it is still better to cover what they safely can than do nothing at all. Please apply this comment to other vapor barrier SWS. | A ground moisture barrier that covers 100% of the exposed crawl space floor, or as much as is accessible while adhering to safe work practices regarding worker access, will be installed | no | Accepted with Modifications | 100% implies that if you can't do 100% then you shouldn't do it at all. |  | No Change | A ground moisture barrier that covers the exposed crawl space floor will be installed | No change
2.0403.2b | Single-Family Homes | Health and Safety | Moisture | Vapor Barriers | Closed Crawl Spaces&mdash;Ground Moisture Barriers | Coverage | An air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary and ground moisture barrier, covering 100% of the exposed crawl space floor, will be installed and sealed to the wall's air and moisture barrier in accordance with ASTM ASTM ASTM International, www.astm.org E1643 and manufacturer's recommendationsGround moisture barrier will be fastened to ground in accordance with manufacturer's recommendations and extend a minimum of 6 inches up the foundation wall | Reduce ground moisture entering the crawl spaceCreate a continuous and durable connection between the wall and ground air and moisture barriers | Not Yet Reviewed | 2017-01-20 | 2017-01-20 | Bruce Hagen | Change to match 2.0403.1b | A ground moisture barrier that covers 100% of the exposed crawl space floor will be installed where accessible. | No | Accepted | Clarifies SWS |  | No Change | An air barrier, the separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary and ground moisture barrier, covering the exposed crawl space floor, will be installed and sealed to the wall's air and moisture barrier in accordance with ASTM International, www.astm.org E1643 and manufacturer's recommendations Ground moisture barrier will be fastened to ground in accordance with manufacturer's recommendations and extend a minimum of 6 inches up the foundation wall | Reduce ground moisture entering the crawl space Create a continuous and durable connection between the wall and ground air and moisture barriers
2.0403.2b | Single-Family Homes | Health and Safety | Moisture | Vapor Barriers | Closed Crawl Spaces&mdash;Ground Moisture Barriers | Coverage | An air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary and ground moisture barrier, covering 100% of the exposed crawl space floor, will be installed and sealed to the wall's air and moisture barrier in accordance with ASTM ASTM ASTM International, www.astm.org E1643 and manufacturer's recommendationsGround moisture barrier will be fastened to ground in accordance with manufacturer's recommendations and extend a minimum of 6 inches up the foundation wall | Reduce ground moisture entering the crawl spaceCreate a continuous and durable connection between the wall and ground air and moisture barriers | Not Yet Reviewed | 2015-12-11 | 2015-12-11 | Charles Kurnik | The title of ASTM E1643 is "Selection, Design, Installation, and Inspection of Water Vapor Retarders Used in Contact with Earth or Granular Fill Under Concrete Slabs". Because this Detail does not relate to placing a moisture barrier under a concrete slab, I believe ASTM E1643 should not be referenced in this spec. Unless a detail specifically relates to placing a moisture barrier under a concrete slab, reference to ASTM E1643 should be removed from all SWS Details where it occurs. | An air barrier and ground moisture barrier, covering 100% of the exposed crawl space floor, will be installed and sealed to the wall's air and moisture barrier in accordance with manufacturer's recommendations | If anything, it will decrease cost - workers will not need to purchase/reference this standard. | Accepted with Modifications | Agreed as this is not covered in E1643, but it is covered in E241. "8.5.2 Vapor Retarders on Exposed Earth in Crawl Spaces— Use of vapor retarders to limit evaporation of soil moisture into the crawlspace air is recognized as one of the most effective means of preventing elevated moisture conditions in crawl- spaces (see ASHRAE Technical Data Bulletin, Vol 10, No. 3). Vapor retarder sheets must resist biological attack and have adequate strength and impedance to vapor transmission." Also took out the 100% covered to align with other changes. |  | No Change | An air barrier, the separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary and ground moisture barrier, covering the exposed crawl space floor, will be installed and sealed to the wall's air and moisture barrier in accordance with ASTM International, www.astm.org E241 and manufacturer's recommendations Ground moisture barrier will be fastened to ground in accordance with manufacturer's recommendations and extend a minimum of 6 inches up the foundation wall | Reduce ground moisture entering the crawl space Create a continuous and durable connection between the wall and ground air and moisture barriers
2.0403.2c | Single-Family Homes | Health and Safety | Moisture | Vapor Barriers | Closed Crawl Spaces&mdash;Ground Moisture Barriers | Material specification | A ground moisture barrier with a rating of no more than 0.1 perm will be used A ground moisture barrier will be used that meets tear and puncture resistance standard ASTM ASTM ASTM International, www.astm.org E1745 Homeowner will be advised that all plastic is biodegradable and will have a life span much shorter than the home (5 years), and it will need replacing to remain effective | Reduce ground vapor entering the crawl space Ensure crawl space is accessible for service and maintenance without destroying the integrity of the moisture barrier | Not Yet Reviewed | 2017-01-16 | 2017-01-16 | State of Alaska... | Where is the science that substantiates this life expectancy of 5 years | Remove 5 year life for poly. |  | Accepted | Agreed |  | No Change | A ground moisture barrier with a rating of no more than 0.1 perm will be used A ground moisture barrier will be used that meets tear and puncture resistance standard ASTM E1745 Homeowner will be advised that all plastic is biodegradable and will have a life span much shorter than the home , and it will need replacing to remain effective | Reduce ground vapor entering the crawl space Ensure crawl space is accessible for service and maintenance without destroying the integrity of the moisture barrier
2.0403.2c | Single-Family Homes | Health and Safety | Moisture | Vapor Barriers | Closed Crawl Spaces&mdash;Ground Moisture Barriers | Material specification | A ground moisture barrier with a rating of no more than 0.1 perm will be usedA ground moisture barrier will be used that meets tear and puncture resistance standard ASTM ASTM ASTM International, www.astm.org E1745Homeowner will be advised that all plastic is biodegradable and will have a life span much shorter than the home (5 years), and it will need replacing to remain effective | Reduce ground vapor entering the crawl spaceEnsure crawl space is accessible for service and maintenance without destroying the integrity of the moisture barrier | Not Yet Reviewed | 2017-01-16 | 2017-01-16 | State of Alaska... | Where is the science that substantiates this life expectancy of 5 years | Remove 5 year life for poly. |  | Accepted | Agreed |  | No Change | A ground moisture barrier with a rating of no more than 0.1 perm will be used A ground moisture barrier will be used that meets tear and puncture resistance standard ASTM E1745 Homeowner will be advised that all plastic is biodegradable and will have a life span much shorter than the home , and it will need replacing to remain effective | Reduce ground vapor entering the crawl space Ensure crawl space is accessible for service and maintenance without destroying the integrity of the moisture barrier
2.0403.2c | Single-Family Homes | Health and Safety | Moisture | Vapor Barriers | Closed Crawl Spaces&mdash;Ground Moisture Barriers | Material specification | A ground moisture barrier with a rating of no more than 0.1 perm will be usedA ground moisture barrier will be used that meets tear and puncture resistance standard ASTM ASTM ASTM International, www.astm.org E1745Homeowner will be advised that all plastic is biodegradable and will have a life span much shorter than the home (5 years), and it will need replacing to remain effective | Reduce ground vapor entering the crawl spaceEnsure crawl space is accessible for service and maintenance without destroying the integrity of the moisture barrier | Not Yet Reviewed | 2017-01-16 | 2017-01-16 | State of Alaska... | Where is the science that substantiates this life expectancy of 5 years | Remove 5 year life for poly. |  | Accepted | Agreed |  | No Change | A ground moisture barrier with a rating of no more than 0.1 perm will be used A ground moisture barrier will be used that meets tear and puncture resistance standard ASTM E1745 Homeowner will be advised that all plastic is biodegradable and will have a life span much shorter than the home , and it will need replacing to remain effective | Reduce ground vapor entering the crawl space Ensure crawl space is accessible for service and maintenance without destroying the integrity of the moisture barrier
2.0403.2e | Single-Family Homes | Health and Safety | Moisture | Vapor Barriers | Closed Crawl Spaces&mdash;Ground Moisture Barriers | Fastening | The air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary and ground moisture barrier will be fastened to the ground to prevent movement in accordance with ASTM ASTM ASTM International, www.astm.org E1643 and manufacturer's recommendations | Prevent movement and uplift of the air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary and ground moisture barrier | Not Yet Reviewed | 2017-01-16 | 2017-01-16 | State of Alaska... | Hundreds of gvb's have been installed in alaska without fasteners without any problem. Our fear is fasteners are punctures in the material. | In reference to redline changes. No fasteners should be needed in a closed crawlspace. | Added fasteners does add cost to labor and material | Rejected | Redline change provides options depending on house conditions. Ballasts do not puncture the barrier. Please provide further clarification to understand how to address.
2.0403.3c | Single-Family Homes | Health and Safety | Moisture | Vapor Barriers | Closed Crawl Spaces&mdash;Vapor Retarders on Walls | Termite inspection gap | Where termite pressure exists, a 3" inspection gap will be maintained from the top of the insulation to the bottom of any wood | Allow for termite detection | Not Yet Reviewed | 2017-01-25 | 2017-01-25 | Kelly Cutchin C... | There is no adequate definition of "where termite pressure exists." We must rely on the locally adopted to codes to determine if termite pressure exists, otherwise one could argue it exists everywhere. | Where code requires, a 3" inspection gap will be maintained from the top of the insulation to the bottom of any wood | no | Accepted with Modifications | Clarifies SWS |  | No Change | Where termite pressure exists or local code requires, a 3" inspection gap will be maintained from the top of the insulation to the bottom of any wood. | Allow for termite detection
2.0601.1c | Single-Family Homes | Health and Safety | Electrical | Knob and Tube Wiring | Knob and Tube Wiring | Isolation and protection | Live knob and tube will not be covered or surrounded; required by the National Electrical Code ( NEC NEC National Electrical Code ) or authority having jurisdictionA licensed electrical contractor will inspect and certify wiring to be safe and place a warning at all entries to the attic about the presence of knob and tube wiringA dam that does not cover the top will be created to separate insulation from the wire path | Ensure occupant safetyPreserve the integrity and safety of the house | Not Yet Reviewed | 2017-01-18 | 2017-01-18 | Jonathan Ballew | Further explanation is needed in this detail. | Redline change. Define what "proper clearance" is. | no. | Rejected | "Proper clearance" is going to be determined by the NEC or AHJ.
2.0601.1c | Single-Family Homes | Health and Safety | Electrical | Knob and Tube Wiring | Knob and Tube Wiring | Isolation and protection | Live knob and tube will not be covered or surrounded; required by the National Electrical Code ( NEC NEC National Electrical Code ) or authority having jurisdictionA licensed electrical contractor will inspect and certify wiring to be safe and place a warning at all entries to the attic about the presence of knob and tube wiringA dam that does not cover the top will be created to separate insulation from the wire path | Ensure occupant safetyPreserve the integrity and safety of the house | Not Yet Reviewed | 2014-05-02 | 2014-05-02 | Rachel Romero | Per Executive Committee, remove "A licensed electrical contractor will inspect and certify wiring to be safe and place a warning at all entries to the attic about the presence of knob and tube wiring". "Proper clearance will be maintained around live knob and tube; required by the National Electrical Code ( NEC ) or authority having jurisdiction Rationale: Defer to the authority having jurisdiction for the inspection requirements. |  |  | Rejected | Already changed in the redline.
2.0601.1d | Single-Family Homes | Health and Safety | Electrical | Knob and Tube Wiring | Knob and Tube Wiring | Replacement | Exposed wiring will be replaced with new appropriate wiring in accordance with the NEC NEC National Electrical Code and local codes Old wiring will be rendered inoperable by licensed electrician in accordance with the NEC NEC National Electrical Code and local codes | Ensure occupant safetyPreserve the integrity and safety of the house | Not Yet Reviewed | 2017-01-18 | 2017-01-18 | Jonathan Ballew | clarification is needed on what is meant by "exposed wiring" | clarification is needed on this detail. Does "exposed" refer to sheathing that has worn off the wire? This detail sounds as though all knob and tube wiring that can be seen must be replaced. | no. | Accepted | Remove exposed since the title is "replacement". Determining hazard has already been completed. |  | No Change | Wiring will be replaced with new appropriate wiring in accordance with the NEC National Electrical Code and local codes Old wiring will be rendered inoperable by licensed electrician in accordance with the NEC National Electrical Code and local codes | Ensure occupant safety Preserve the integrity and safety of the house
2.0601.1d | Single-Family Homes | Health and Safety | Electrical | Knob and Tube Wiring | Knob and Tube Wiring | Replacement | Exposed wiring will be replaced with new appropriate wiring in accordance with the NEC NEC National Electrical Code and local codesOld wiring will be rendered inoperable by licensed electrician in accordance with the NEC NEC National Electrical Code and local codes | Ensure occupant safetyPreserve the integrity and safety of the house | Not Yet Reviewed | 2017-01-25 | 2017-01-25 | Kelly Cutchin C... | Clarifying when replacement is called for. | Change first line to read: When deemed necessary by electrician, exposed wiring will be replaced with new appropriate wiring in accordance with the NEC and local codes | no | Rejected | Decision has already been made since the title is "Replacement" CK: After meeting with Kelly and Jonathan, we are trying to make this Specification align with the redline in the Specification above (ie, adding "If required"). Recommend changing adjudication to "Accept", from "Reject"
2.0701.1a | Single-Family Homes | Health and Safety | Occupant Education and Access | Basements and Crawl Spaces | Crawl Spaces&mdash;Providing Access | Access | Crawl space will be accessible in accordance with 2012 IRC IRC International Residential Code R408.4Access to mechanical equipment located in the crawl space will be in accordance with 2012 IRC IRC International Residential Code M1305.1.4Service and maintenance of the crawl space and equipment will be performed without risk of damage to the thermal barrier, air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary , and ground moisture barrier in accordance with 2012 IRC IRC International Residential Code N1102.2.4 and 2012 IRC IRC International Residential Code AF103.4.10 | Provide crawl space accessMaintain integrity of the crawl space system | Not Yet Reviewed | 2017-01-25 | 2017-01-25 | Kelly Cutchin C... | This is unreasonable in many retrofit situations. To bring the crawl space access to equipment up to code would be monumental in many cases. But if they are providing new access, that access should be up to code. | Change title to: Providing New Access | no | Accepted | Ok |  | Crawl Spaces - Providing New Access | No Change | No Change
2.0701.1b | Single-Family Homes | Health and Safety | Occupant Education and Access | Basements and Crawl Spaces | Crawl Spaces&mdash;Providing Access | Lock | A lockable access will be provided if access is from the exterior | Control access and prevent intruders | Not Yet Reviewed | 2017-01-25 | 2017-01-25 | Kelly Cutchin C... | Some residents prefer a catchable, but not lockable, access. They worry about losing the key or combination. | Change title to - Security Spec to - At client's/resident's discretion, a lockable access will be provided if access is from the exterior. | no | Accepted | Ok |  | Security | At client's/resident's discretion, a lockable access will be provided if access is from the exterior. | No Change
2.0702.1c | Single-Family Homes | Health and Safety | Occupant Education and Access | Installed Equipment | Warranty and Service Agreement | General conditions | At a minimum, the following concerns and warnings will be addressed within the warranty:Possible drying and shrinking effectsStorage of hazardous and flammable materialsMold | Educate occupants on potential hazards | Not Yet Reviewed | 2017-01-25 | 2017-01-25 | Kelly Cutchin C... | Some of these wouldn't apply to, say, a refrigerator replacement. | Change first line to read: At a minimum, the following concerns and warnings will be addressed within the warranty, as applicable to the work being warrantied,: | no | Accepted | Ok |  | No Change | At a minimum, the following concerns and warnings will be addressed within the warranty, as applicable to the work being warrantied: Possible drying and shrinking effects Storage of hazardous and flammable materials Mold | Educate occupants on potential hazards
2.0702.1c | Single-Family Homes | Health and Safety | Occupant Education and Access | Installed Equipment | Warranty and Service Agreement | General conditions | At a minimum, the following concerns and warnings will be addressed within the warranty: Possible drying and shrinking effects Storage of hazardous and flammable materialsMold | Educate occupants on potential hazards | Not Yet Reviewed | 2017-01-18 | 2017-01-18 | Jonathan Ballew | This detail needs clarification. | I'm not sure what is meant by this detail. "storage of hazardous and flammable materials"? | no. | Rejected | Not enough detail in comment propose new language change, please clarify if issue is with hazardous material or with storage in this spec?
3.1001.9f | Multifamily Homes | Air Sealing | Attics | Penetrations and Chases | Sealing Access Doors and Similar Intentional Penetrations | Installation | Access hatches will be insulated with noncompressible insulation to the same R-value as adjoining insulated assemblyAttic hatch rough opening will be surrounded with a durable protective baffle that is higher than the level of the surrounding attic floor insulation | Achieve uniform R-value on the attic door or hatch Achieve uniform R-value on the attic floorPrevent loose attic floor insulation from entering the living area | Not Yet Reviewed | 2017-01-02 | 2017-01-02 | Jeffrey Shannon | In order to serve as a protective barrier, it must be constructed of rigid material. Without this specification, batt insulation could be used. Since batt insulation is compressible, it would fail to meet the requirement at the first occurrence of egress to the attic. | Attic hatch rough opening will be surrounded with a durable protective dam or baffle made of wood or rigid foamboard that is higher than the level of the surrounding attic floor insulation | No cost if the requirement is met | Accepted with Modifications | Added language describing rigid protective baffles |  | No change | Access hatches will be insulated with noncompressible insulation to the same R-value as adjoining insulated assembly Attic hatch rough opening will be surrounded with a durable, rigid protective baffle that is higher than the level of the surrounding attic floor insulation | No change
3.1001.9f | Multifamily Homes | Air Sealing | Attics | Penetrations and Chases | Sealing Access Doors and Similar Intentional Penetrations | Installation | Access hatches will be insulated with noncompressible insulation to the same R-value as adjoining insulated assemblyAttic hatch rough opening will be surrounded with a durable protective baffle that is higher than the level of the surrounding attic floor insulation | Achieve uniform R-value on the attic door or hatch Achieve uniform R-value on the attic floorPrevent loose attic floor insulation from entering the living area | Not Yet Reviewed | 2017-01-02 | 2017-01-02 | Jeffrey Shannon | Without a warranty, there is no means of assuring the measure will be operational for the expected service life. | Completed measure will contain a warranty for a service life of 20 years. |  | Rejected | WX provides a one year warranty. NREL Comment: Also consider the warranty market-rate contractors might provide
3.1005.3c | Multifamily Homes | Air Sealing | Attics | Other Ceiling Materials | Air Sealing Complex Ceiling Planes | Spanning material selection | Materials used to span elevation changes will be rigid and self-supporting over the distance spannedMaterials will be consistent with existing or intended fire-resistance assembliesMaterials will be compatible with adjacent materials and with any proposed insulation designed to come in contact with it The perimeters of all materials installed to span elevation changes will be sealed on all exposed edges with compatible sealantsSeals will be used that prevent visible air movement using chemical smoke at 50 pascals of pressure difference |  | Not Yet Reviewed | 2016-12-08 | 2016-12-08 | Kelly Cutchin C... | Every spec must have an objective. | Not sure - there's no text in the "Objective(s)" column. This must be an oversight. Maybe the language exists somewhere and can be added. | Not likely. | Accepted | Added objective language |  | No change | No change | Prevent air leakage from complex ceiling planes. Provide airtight, durable seal that does not move, bend, or sag and can support the weight of installed insulation
3.1602.1c | Single-Family Homes | Air Sealing | Ducts | Duct Sealing | Air Sealing Duct System | Existing component to existing component | Fiberglass mesh and mastic will overlap temporary tape by at least 1" on all sidesFiberglass mesh and mastic will become the primary sealSeams, cracks, joints, holes, and penetrations larger than ¾" will be repaired using rigid duct materialFiberglass mesh and mastic will overlap repair joint by at least 1" on all sidesFiberglass mesh and mastic will be the primary seal | Eliminate air leakage into or out of ducts and plenumsEnsure adhesion of primary seal (fiberglass mesh and mastic) to the ductReinforce sealSupport fiberglass mesh and mastic during curing | Not Yet Reviewed | 2016-05-17 | 2016-05-18 | Colorado Energy... | Colorado seeks to use fiber embedded UL 181 A-M and B-M mastic alone for cracks, seams, or holes in all duct systems 1/4" or less and for areas that are greater than 1/4" mastic and fiberglass tape will be used. Mastic alone is acceptable for specification 3.1602.1b, new component to existing component yet for "existing component to existing the specification only allows mastic and mesh tape. Based on fiber embedded mastic manufactures product specifications which is UL 181 a-m and b-m approved, mastic may be used on holes or cracks up to 1/2". If needed, mastic manufacture info sheets can be submitted. In 3.1602.1c it states that “Fiberglass mesh and mastic will become the primary seal”, so all duct sealing performed must be with fiberglass mesh and mastic. However specifications 4.1601.2b, 4.1601.1h, and 3.1501.1b do not require fiberglass mesh, only that the sealing be done with “UL 181 B-M mastic (adhesives) or mastic- plus-embedded-fabric systems. | Mastic alone will be acceptable for holes less than ¼" that are more than 10' from air handler. | This change will not increase the cost of duct sealing. The change would actually bring duct sealing costs down. Both the labor and materials cost would decrease with this addition as adding mesh tape and additional mastic to cover tape adds around 1.25 hours to each duct sealing job. | Accepted with Modifications | Consistency with other specifications |  | No change | Seams, cracks, joints, holes, and penetrations less than ¼" will be sealed using UL 181 fiber-embedded mastic Seams, cracks, joints, holes, and penetrations between ¼" and ¾" will be sealed in two stages: * They will be backed using temporary tape (e.g., foil tape) as a support prior to sealing * They will be sealed using fiberglass mesh and mastic Seams, cracks, joints, holes, and penetrations larger than ¾" will be repaired using rigid duct material Mastic will overlap repair joint or existing temporary tape by at least 1" on all sides | No change
4.1001.1a | Single-Family Homes | Insulation | Attics | General Preparation | Non-Insulation Contact (IC) Recessed Light | Air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary system | A fire-rated air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary system (i.e., equivalent to 5/8 fire code gypsum wallboard) will be used to separate non- IC IC Insulation contact rated recessed lights from insulation, using one of the methods below:A fire-rated airtight closure taller than surrounding attic insulation will be placed over non- IC IC Insulation contact rated recessed lightsORThe non- IC IC Insulation contact rated light fixture will be replaced with an airtight and IC IC Insulation contact - rated fixtureORThe fixture(s) may be replaced with surface mounted fixture and opening sealedORAir sealing measures as approved by the authority having jurisdiction | Prevent a fire hazardPrevent air leakage through fixture | Not Yet Reviewed | 2017-01-18 | 2017-01-18 | Jonathan Ballew | These are becoming more and more popular and can be completed cost effectively. | This detail should included air tight LED trim kits. | no | Accepted | Clarifies SWS |  | No change | A fire-rated air barrier system (i.e., equivalent to 5/8 fire code gypsum wallboard) will be used to separate non- IC rated recessed lights from insulation, using one of the methods below: A fire-rated airtight closure taller than surrounding attic insulation will be placed over non- IC rated recessed lights OR The non- IC rated light fixture will be replaced with an airtight IC - rated fixture or insert OR The fixture(s) may be replaced with surface mounted fixture and opening sealed OR Air sealing measures as approved by the authority having jurisdiction | No Change
4.1001.2c | Single-Family Homes | Insulation | Attics | General Preparation | Knob and Tube Wiring | Isolate or replace | Live knob and tube will not be covered or surrounded; required by the National Electrical Code ( NEC NEC National Electrical Code ) or authority having jurisdictionA licensed electrical contractor will inspect and certify wiring to be safe and place a warning at all entries to the attic about the presence of knob and tube wiringA dam that does not cover the top will be created to separate insulation from the wire pathORKnob and tube wiring will be replaced with new appropriate wiring by a licensed electrician in accordance with local codesRemaining knob and tube wiring will be rendered inoperable by licensed electrician in accordance with local codes | Ensure work can be completed safelyProtect occupant and houseEnsure future work can be done safelyPrevent the overheating of the wiring | Not Yet Reviewed | 2017-01-25 | 2017-01-25 | Kelly Cutchin C... | 2 SWS addressing same topic should line up, and local codes that allow for more thorough insulation when deemed safe should be allowed in the SWS. | Suggest aligning language between this and the K&T SWS in the H&S section. Also, if it has been deemed safe by a licensed electrician, some jurisdictions allow all around damming then covering the dammed wiring with insulation. Add language to allow for this. | no | Accepted | Allign similar SWS specifications |  | No change | Proper clearance will be maintained around live knob and tube as required by the National Electrical Code ( NEC ) or authority having jurisdiction When required, a dam that does not cover the top will be created to separate insulation from the wire path | No change
4.1003.4d | Single-Family Homes | Insulation | Attics | Attic Ceilings | Cape Cod Side Attic Roof&mdash;Dense Pack Installation | Onsite documentation | A dated receipt signed by the installer will be provided that includes:Insulation typeCoverage areaR-valueInstalled thickness and minimum settled thicknessNumber of bags installed in accordance with manufacturer specifications | Document job completion to contract specificationsConfirm amount of insulation installedEnsure ability to match bags required for total area completedComply with 16 CFR 460.17 | Not Yet Reviewed | 2017-01-20 | 2017-01-20 | Bruce Hagen | It doesn't show up in other tasks and 4.1003.4e should suffice | Delete this section | No | Rejected | 4.1003.4d meets requirements of 16 CFR 460.17. Optionally could delete 4.1003.4e based on redundancy.
4.1003.9b | Manufactured Housing | Insulation | Attics | Attic Ceilings | Installing Fiberglass Blown Insulation for Flat, Bowed, or Vaulted Ceilings (via Exterior Access from Top of Roof) | Attic access | Access to the attic cavity will be created using one of these methods: Drilling Cutting Continuous slicing along the center line (at the highest point of the roof )Access location will be placed to allow for consistent and uniform coverage of installed insulation throughout the attic assemblyThere will be, at a minimum, one opening between each roof trussOpenings will be large enough to accommodate the chosen fill tubeIf subsheathing is present, access will be gained through subsheathingAttic will be visually inspected for the location of existing insulation, wiring, flues, obstructions, hazards, and construction type | Create access to the full attic cavityMaintain the integrity of the roof trussProtect roof from wind damage during installationDetermine technique for installing insulation | Not Yet Reviewed | 2015-12-08 | 2015-12-08 | Kelly Cutchin C... | Many technicians, especially in cold climates, access the roof through gable end vents. This is less risky than cutting through the roof. | Suggest drafting new detail to address access through gable ends. Could borrow much language from this SWS. | No. Decrease. | Accepted with Modifications | New Detail developed for Installing Fiberglass Blown Insulation for Flat, Bowed, or Vaulted Ceilings (via Gable End Access) and is numbered 4.1003.15. Embedded Word document attachment shows changes to 4.1003.15.
4.1005.2d | Single-Family Homes | Insulation | Attics | Attic Floors | Accessible Floors&mdash;Loose Fill Installation | Onsite documentation | A dated receipt signed by the installer will be provided that includes:Insulation typeCoverage areaR-valueInstalled thickness and settled thicknessNumber of bags installed in accordance with manufacturer specifications | Document job completion to contract specificationsConfirm amount of insulation installedEnsure ability to match bags required for total area completedComply with 16 CFR 460.17 | Not Yet Reviewed | 2017-01-20 | 2017-01-20 | Bruce Hagen | To remain consistent with other sections. | Documentation of material and R-value will be provided to occupant | No | Accepted | SWS consistency, added new specification 4.1005.2e, Occupant Education, which follows the same language as 4.1001.4e, Occupant Education |  | New Spec 4.1005.2e Occupant education | New Spec Documentation of material and R-value will be provided to occupants | New Spec Provide occupant with documentation of installation
4.1005.5b | Single-Family Homes | Insulation | Attics | Attic Floors | Enclosed Bonus Room Floor Over Unconditioned Space&mdash;Dense Pack Installation | Fill floors | Each cavity will be 100% filled to consistent density:Cellulose material will be installed to a minimum density of 3.5 pounds per cubic footLoose fiberglass material will be installed and will be specifically approved for air flow resistance to a minimum density per the manufacturer's recommendationsThe number of bags installed will be confirmed and will match the number required on the coverage chartInsulation will be verified to prevent visible air movement using chemical smoke at 50 pascals of pressure difference | Eliminate voids and settlingMinimize framing cavity air flows | Not Yet Reviewed | 2017-01-20 | 2017-01-20 | Bruce Hagen | To be consistent with other sections. | Insulation will be verified to prevent visible air movement at 50 pascals of pressure difference using chemical smoke, IR scans, or other approved verification method. | No | Accepted with Modifications | modified language to create consistency within the SWS |  | No change | Each cavity will be 100% filled to consistent density: * Cellulose material will be installed to a minimum density of 3.5 pounds per cubic foot or to a maximum density structurally allowable * Loose fiberglass material will be installed and will be specifically approved for air flow resistance to a minimum density per the manufacturer's recommendations The number of bags installed will be confirmed and will match the number required on the coverage chart Insulation will be verified to prevent visible air movement at 50 pascals of pressure difference using chemical smoke or other approved verification method by the authority having jurisdiction | No change
4.1005.6a | Single-Family Homes | Insulation | Attics | Attic Floors | Enclosed Attic Storage Platform Floor&mdash;Dense Pack Installation | Fill floors | Each cavity will be 100% filled to consistent density:Cellulose material will be installed to a minimum density of 3.5 pounds per cubic footLoose fiberglass material will be installed and will be specifically approved for air flow resistance to a minimum density per the manufacturer's recommendationsThe number of bags installed will be confirmed and will match the number required on the coverage chartInsulation will be verified to prevent visible air movement using chemical smoke at 50 pascals of pressure difference | Eliminate voids and settlingMinimize framing cavity air flows | Not Yet Reviewed | 2017-01-18 | 2017-01-18 | Jonathan Ballew | this would align the verification methods for this detail and 4.1003.2a | "insulation will be verified using IR scan, chemical smoke, or other approved verification method" | no | Accepted with Modifications | Modified redline language to include AHJ language |  | No change | Each cavity will be 100% filled to consistent density: * Cellulose material will be installed to a minimum density of 3.5 pounds per cubic foot or to a maximum density structurally allowable * Loose fiberglass material will be installed and will be specifically approved for air flow resistance to a minimum density per the manufacturer's recommendations The number of bags installed will be confirmed and will match the number required on the coverage chart Insulation will be verified to prevent visible air movement at 50 pascals of pressure difference using chemical smoke or other approved verification method by the authority having jurisdiction | No change
4.1005.6c | Single-Family Homes | Insulation | Attics | Attic Floors | Enclosed Attic Storage Platform Floor&mdash;Dense Pack Installation | Onsite documentation | A dated receipt signed by the installer will be provided that includes:Coverage areaThicknessR-value | Document job completion to contract specificationsConfirm amount of insulation installedComply with 16 CFR 460.17 | Not Yet Reviewed | 2017-01-20 | 2017-01-20 | Bruce Hagen | To remain consistent with other sections | Documentation of material and R-value will be provided to occupant | No | Accepted | Executive committee (comment recommends adding 4.1005.6d - Occupant Education); make all onsite documentation consistent in SWS |  | New Spec 4.1005.6d Occupant education | New Spec Documentation of material and R-value will be provided to occupants | New Spec Provide occupant with documentation of installation
4.1006.1a | Single-Family Homes | Insulation | Attics | Attic Openings | Pull-Down Stairs | Installation | Hatches will be insulated to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assemblyPull-down stair rough opening will be surrounded with a durable dam that is higher than the level of the attic floor insulationCounter-weights should be considered to ease accessibility for excessively heavy hatches | Achieve uniform R-valuePrevent loose insulation from entering the living area | Not Yet Reviewed | 2017-01-16 | 2017-01-16 | Andrew Long | Need stated minimum insulation or contractors will abuse the opportunity to use R-3 tent kits or flimsy, low R-value coffin boxes. You can’t have batt insulation for any attic pull down stairs. Batt compresses and loses the R-Value. Too many contractors try to get away on the cheap by using batt. The homeowner deserves better! Same goes for the protective baffle. What do you think will happen to a barrier made of batt? How much loose fill will it hold back once someone leans on the batt? Get rid of the batt and make it an effective and lasting measure. | Folding ladders will be insulated to the same the R-Value of the adjoining insulated assembly with rigid foamboard. If there is limited clearance, it will be insulated to at least R-20. The Pull-down stair rough opening must have a durable protective barrier made or wood or rigid foamboard that is higher than the level of the attic floor insulation. | Yes it will, but only a minimal increase. With amount of energy saved and providing a higher quality solution for the homeowner, the negligible cost increase is well worth it for the homeowner. | Accepted with Modifications | Modified to include Attic-side enclusure and rigid dam language |  | No change | Attic-side enclosure will be insulated to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assembly Pull-down stair rough opening will be surrounded with a durable, rigid dam that is higher than the level of the attic floor insulation Counter-weights should be considered to ease accessibility for excessively heavy hatches | No change
4.1006.1a | Single-Family Homes | Insulation | Attics | Attic Openings | Pull-Down Stairs | Installation | Hatches will be insulated to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assemblyPull-down stair rough opening will be surrounded with a durable dam that is higher than the level of the attic floor insulationCounter-weights should be considered to ease accessibility for excessively heavy hatches | Achieve uniform R-valuePrevent loose insulation from entering the living area | Not Yet Reviewed | 2017-01-02 | 2017-01-02 | Jeffrey Shannon | Eliminating the requirement for rigid foamboard is a mistake and should be reversed. There are many ways that the batt insulation can be compressed which will cause the insulating value to fail to meet the max amount structurally available. In most cases and particularly where there is limited space, the batt insulation would most assuredly be compressed during the installation of the measure. I noted the reference of this section to the IECC R402.2.4. This section requires the protective dam to be constructed of wood or equivalent material. The same wording should be used in the SWS. | Pull-down stairs will be insulated with rigid foamboard to the maximum R-Value structurally allowable up to the R-Value of the adjoining insulated assembly, but in no case less than R-20. Pull-down stair rough opening will be surrounded with a durable dam made or wood or rigid foamboard that is higher than the level of the attic floor insulation. | It is a minimal cost. It is an essential item because without the standard the insulation and dam will not meet the stated requirements. | Accepted with Modifications | Modified to include Attic-side enclusure and rigid dam language |  | No change | Attic-side enclosure will be insulated to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assembly Pull-down stair rough opening will be surrounded with a durable, rigid dam that is higher than the level of the attic floor insulation Counter-weights should be considered to ease accessibility for excessively heavy hatches | No change
4.1006.1a | Single-Family Homes | Insulation | Attics | Attic Openings | Pull-Down Stairs | Installation | Hatches will be insulated to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assemblyPull-down stair rough opening will be surrounded with a durable dam that is higher than the level of the attic floor insulationCounter-weights should be considered to ease accessibility for excessively heavy hatches | Achieve uniform R-valuePrevent loose insulation from entering the living area | Not Yet Reviewed | 2016-12-16 | 2016-12-16 | Jim Melesky | The title of this section is pull-down stairs and it should replace the term hatches in order to eliminate confusion. The existing wording of maximum allowable insulation allows for interpretation of contractors as to what they might perceive or believe that amount might be, allowing the use of low R-value products and measures. The IECC establishes a minimum R-value of R-30. The insulating material must be non-compressible. This is consistent with the referenced section of the IECC. In addition, the pull-down stair is a passage way from one portion of the structure to another. It must be assumed that this opening will be used over time for maintenance and other purposes. Per the manufacturers' installation instructions for batt insulation, compression of the insulating material will reduce the R-value. When the insulating measure is opened and placed down in the attic, it must be assumed that it will be placed in a position to compress the insulation. That will immediately compromise the R-value and render the measure non-compliant with the requirement. For limited clearance sites, this compression of the insulation is almost an assured incidence even during the installation. Rigid foamboard ensures that the insulating value will be reliable for the expected service life of the measure while the term equivalent material allows for future products with consistent properties required. Regarding the use of counterweights, that seems reasonable for constructed measures. However, there was a comment posted for the last edition which posited that rigid foamboard was a concern for elderly due to the weight of the material. That notion is not consistent with the attributes of the existing material. Expanded and extruded polystyrene material are lightweight. The heaviest component of an existing commercially available R-38 product weighs less than 13 lb.-comparable to the weight of an infant. | Pull-down stairs will be insulated to the R-value of the adjoining insulated assembly. In the event of low clearance, the measure will insulated to a minimum of R-30. The insulating material for this measure must be non-compressible, i.e. rigid foamboard or equivalent material. Pull-down stair rough opening will be surrounded by a durable dam, made of wood or equivalent dense material that is higher than the level of the attic floor insulation. Counterweights should be considered to ease accessibility for excessively heavy measures for pull-down stairs. | There is no cost for clarification of the name or the minimum R-value required. It only eliminates the risk of poor interpretation. Rigid foam is more expensive that batt insulation. However, for this small area, it is a minimal cost. Further, it is essential for the integrity of the overall measure. The measure is only as good as its weakest component. If R-value is important, then the material used must be reliable to provide that stated value. | Accepted with Modifications | Modified to include Attic-side enclusure and rigid dam language |  | No change | Attic-side enclosure will be insulated to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assembly Pull-down stair rough opening will be surrounded with a durable, rigid dam that is higher than the level of the attic floor insulation Counter-weights should be considered to ease accessibility for excessively heavy hatches | No change
4.1006.1a | Single-Family Homes | Insulation | Attics | Attic Openings | Pull-Down Stairs | Installation | Hatches will be insulated to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assemblyPull-down stair rough opening will be surrounded with a durable dam that is higher than the level of the attic floor insulationCounter-weights should be considered to ease accessibility for excessively heavy hatches | Achieve uniform R-valuePrevent loose insulation from entering the living area | Not Yet Reviewed | 2017-01-18 | 2017-01-18 | John Leffler | You can’t give wiggle room on two important insulating issues- 1) The insulating material must be non-compressible, i.e. no batt. Everyone knows that batt will be compressed if used for pull down stairs and the R-Value will be lost. 2) Without a stated minimum, some contractors will use phony clearance problems as an excuse for low R-value solutions. I have seen it in both utility and Wx programs. If you expect a protective barrier to be useful, it can’t be made of batt. It is an old, cheap legacy approach that I thought was finally put to rest. Again, it is a cost cutting way for a contractor, but a bad solution for the customer. R-20 can less than 4 inches of rigid foam-that should fit over any pull down ladder or a person can’t use the ladder. | Pull down folding ladders will be insulated to the same the R-Value of the adjoining insulated assembly with rigid foamboard. If there is limited clearance, it will be insulated to at least R-20. A durable protective barrier made or wood or rigid foamboard that is higher than the level of the attic floor insulation must be installed around the pull-down folding stair rough opening. | Considering the size of the area that this addresses, it is not a cost consideration, particularly when the impact on the homeowner is considered. | Accepted with Modifications | Modified to include Attic-side enclusure and rigid dam language |  | No change | Attic-side enclosure will be insulated to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assembly Pull-down stair rough opening will be surrounded with a durable, rigid dam that is higher than the level of the attic floor insulation Counter-weights should be considered to ease accessibility for excessively heavy hatches | No change
4.1006.1a | Single-Family Homes | Insulation | Attics | Attic Openings | Pull-Down Stairs | Installation | Hatches will be insulated to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assemblyPull-down stair rough opening will be surrounded with a durable dam that is higher than the level of the attic floor insulationCounter-weights should be considered to ease accessibility for excessively heavy hatches | Achieve uniform R-valuePrevent loose insulation from entering the living area | Not Yet Reviewed | 2017-01-17 | 2017-01-17 | Kevin Bolger | My main concern is my customers. They are the ones these standards are supposed to benefit and protect. Without specific R-Values and materials required by the standards it allows old legacy measures to be used. Although maintaining consistent R-values is very important the material used to do so is even more important. Batt insulation and other compressible insulations do not hold up for the long term. Anyone who has crawled in an attic knows that batt insulation that is exposed to air flow of conditioned and un-conditioned air will have mold grow on it. It is only a matter of time. This mold causes many problems for the home owner. Indoor air quality being one of the first things to suffer once introduced to the attic. We cannot allow a relaxation of standards that helps introduce this kind of problem into homes. So many people are counting on us to do the correct work. | Pull down ladder openings will be insulated with rigid foam or equivalent non-compressible material to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assembly, but no less than R-20. Pull-down stair rough opening will be surrounded with a durable dam that is higher than the level of the attic floor insulation and constructed of wood, rigid foam board, or other solid material. | Cost is an issue in the absence of value. The minor increase in cost of using rigid insulation cannot be compared to value of my customers health and safety. In addition, the cost increase of rigid is minimal in comparison to the cost of proper mold remediation. | Accepted with Modifications | Modified to include Attic-side enclusure and rigid dam language |  | No change | Attic-side enclosure will be insulated to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assembly Pull-down stair rough opening will be surrounded with a durable, rigid dam that is higher than the level of the attic floor insulation Counter-weights should be considered to ease accessibility for excessively heavy hatches | No change
4.1006.1a | Single-Family Homes | Insulation | Attics | Attic Openings | Pull-Down Stairs | Installation | Hatches will be insulated to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assemblyPull-down stair rough opening will be surrounded with a durable dam that is higher than the level of the attic floor insulationCounter-weights should be considered to ease accessibility for excessively heavy hatches | Achieve uniform R-valuePrevent loose insulation from entering the living area | Not Yet Reviewed | 2016-12-29 | 2016-12-29 | Mike Hight | Removing the requirement for rigid foamboard will result in ineffective measures made of batt insulation. That was a legacy measure that the IECC and the first edition of the SWS rightly eliminated. Batt insulation will compress as soon as a person enters the attic. That will lower the protective dam making it non-compliant with the standard. As soon as the pull down stair cover is set on the attic floor, the batt insulation will again compress which reduces the R-value. This again makes the R-value non compliant. Where there is limited space, setting the R-value at R-20 seems like a reasonable level and assures an acceptable insulating value. This will protect the resident from very low R-value per-fab kits that have been widely used for years that are not consistent with the intent of this section. | Pull-down folding ladders will be insulated to the same the R-Value of the adjoining insulated assembly with rigid foamboard. If there is limited clearance, it will be insulated to a minimum of R-20. Pull-down stair rough opening will be surrounded with a durable protective barrier made or wood, rigid foamboard or equivalent material that is higher than the level of the attic floor insulation. | If you want to meet the standards, you need to use the proper materials. Cost is very small. | Accepted with Modifications | Modified to include Attic-side enclusure and rigid dam language |  | No change | Attic-side enclosure will be insulated to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assembly Pull-down stair rough opening will be surrounded with a durable, rigid dam that is higher than the level of the attic floor insulation Counter-weights should be considered to ease accessibility for excessively heavy hatches | No change
4.1006.1a | Single-Family Homes | Insulation | Attics | Attic Openings | Pull-Down Stairs | Installation | Hatches will be insulated to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assemblyPull-down stair rough opening will be surrounded with a durable dam that is higher than the level of the attic floor insulationCounter-weights should be considered to ease accessibility for excessively heavy hatches | Achieve uniform R-valuePrevent loose insulation from entering the living area | Not Yet Reviewed | 2017-01-10 | 2017-01-10 | RW DAVIS | Justification The changes for pull down ladders in the latest edition water down the standards and remove important clarity that was written into the 2013 edition of the SWS. It is particularly concerning since the SWS standards for the attic pull down stairs reference IECC R402.2.4. This section requires the wood or equivalent protective dam and non-compressible insulation for the measure. With specific standards removed, many will return to using inadequate measures with low R-value measures and others using batt insulation. First, the attic pull down ladders are portals from one part of the residence to another. Like any other door or means of egress, it must be assumed that they will be used. Manufacturers installation instructions for batt insulation make it clear that compression of the insulation will reduce the insulating value. The removable section of any measure for any attic access will be placed down and compress batt insulation. Therefore, the use of batt insulation for the insulating component and protective dam are very bad ideas and contrary to the purpose of the standards. Secondly, whoever believes rigid foamboard is too heavy must not have ever used expanded or extruded polystyrene products. They are lightweight and provide high R-value that do not pose a risk to seniors. Rigid foam board is also currently required I the SWS for whole house fans and hatches in multi-family residences. Cost Justification Although pull down ladders represent a large area of energy loss, they are relatively small in size. The cost for building solutions out of foam board or using prefab kits that meet the above requirements is minimal and is justified by the energy savings. | Section 4.1006.1a New Text Pull down ladder openings will be insulated with rigid foam or equivalent non-compressible material to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assembly, but in no case less than R-30. Pull-down stair rough opening will be surrounded with a durable dam that is higher than the level of the attic floor insulation and constructed of wood, rigid foam board of a minimum of 2 lb. density or an equivalent material. Counter-weights should be considered to ease accessibility for excessively heavy hatch measures that are in excess of 20 lb. |  | Accepted with Modifications | Modified to include Attic-side enclusure and rigid dam language |  | No change | Attic-side enclosure will be insulated to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assembly Pull-down stair rough opening will be surrounded with a durable, rigid dam that is higher than the level of the attic floor insulation Counter-weights should be considered to ease accessibility for excessively heavy hatches | No change
4.1006.1b | Single-Family Homes | Insulation | Attics | Attic Openings | Pull-Down Stairs | Sealing | Entire pull-down stair assembly will be covered with an airtight and removable/openable enclosure inside the attic spacePull-down stair frame will be caulked, gasketed, weatherstripped, or otherwise sealed with an air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary material, suitable film, or solid material that allows attic door operation | Prevent air leakage | Not Yet Reviewed | 2017-01-10 | 2017-01-10 | RW DAVIS | Justification It is important to have frictionally engaged components included as a way to air seal. Frictionally engaged components are a highly effective and acceptable way to achieve the needed air seal. Further, frictionally engaged components is included in the section for hatches and should be included for pull down ladders. Cost Justification There is no increase to the cost. | Section 4.1006.1b New Text Pull-down stair frame will be caulked, gasketed, weatherstripped, or otherwise sealed with an air barrier material, suitable film, frictionally engaging components or solid material that allows attic door operation. |  | Accepted | Consistency with other specifications |  | No change | Entire pull-down stair assembly will be covered with an airtight and removable/openable enclosure inside the attic space Pull-down stair frame will be caulked, gasketed, weatherstripped, or otherwise sealed with an air barrier material, suitable film, frictionally engaging components or solid material that allows attic door operation | Prevent air leakage Insulation and air barrier must be aligned
4.1006.1c | Single-Family Homes | Insulation | Attics | Attic Openings | Pull-Down Stairs | Durability | Completed measure will meet a minimum expected service life of 20 years | Ensure a minimum expected service life | Not Yet Reviewed | 2017-01-16 | 2017-01-16 | Andrew Long | Without a warranty or contractor guaranty, the very important service life will be real for the homeowner. | Completed measure will meet a minimum expected service life of 20 years, backed by a manufacturer’s warranty or contractor guaranty. | No cost increase for a warranty | Accepted with Modifications | WX provides a one year warranty as specified under Detail Warranty and Service Agreement (2.0702.1) |  | Delete | Delete | Delete
4.1006.1c | Single-Family Homes | Insulation | Attics | Attic Openings | Pull-Down Stairs | Durability | Completed measure will meet a minimum expected service life of 20 years | Ensure a minimum expected service life | Not Yet Reviewed | 2017-01-02 | 2017-01-02 | Jeffrey Shannon | Without a warranty, the durability to last 20 years will have no means of confidence which also makes it a subjective quality. Requiring a warranty assures consistent quality. As a contractor, it establishes a level playing field when we compete against low quality contractors. | Completed measure will be warranted for a minimum of 20 years | Without a warranty, the durability to last 20 years will have no means of confidence which also makes it a subjective quality. Requiring a warranty assures consistent quality. As a contractor, it establishes a level playing field when we compete against low quality contractors. | Accepted with Modifications | WX provides a one year warranty as specified under Detail Warranty and Service Agreement (2.0702.1) |  | Delete | Delete | Delete
4.1006.1c | Single-Family Homes | Insulation | Attics | Attic Openings | Pull-Down Stairs | Durability | Completed measure will meet a minimum expected service life of 20 years | Ensure a minimum expected service life | Not Yet Reviewed | 2017-01-02 | 2017-01-02 | Jeffrey Shannon | Without a warranty, the durability to last 20 years will have no means of confidence which also makes it a subjective quality. Requiring a warranty assures consistent quality. As a contractor, it establishes a level playing field when we compete against low quality contractors. Cost | Completed measure will be warranted for a minimum of 20 years | No cost if the measure meets the standards. | Accepted with Modifications | WX provides a one year warranty as specified under Detail Warranty and Service Agreement (2.0702.1) |  | Delete | Delete | Delete
4.1006.1c | Single-Family Homes | Insulation | Attics | Attic Openings | Pull-Down Stairs | Durability | Completed measure will meet a minimum expected service life of 20 years | Ensure a minimum expected service life | Not Yet Reviewed | 2017-01-02 | 2017-01-02 | Jeffrey Shannon | Without a warranty, the durability to last 20 years will have no means of confidence which also makes it a subjective quality. Requiring a warranty assures consistent quality. As a contractor, it establishes a level playing field when we compete against low quality contractors. Cost | Completed measure will be warranted for a minimum of 20 years | No cost if the measure meets the standards. | Accepted with Modifications | WX provides a one year warranty as specified under Detail Warranty and Service Agreement (2.0702.1) |  | Delete | Delete | Delete
4.1006.1c | Single-Family Homes | Insulation | Attics | Attic Openings | Pull-Down Stairs | Durability | Completed measure will meet a minimum expected service life of 20 years | Ensure a minimum expected service life | Not Yet Reviewed | 2017-01-18 | 2017-01-18 | John Leffler | A warranty is the only way to protect a homeowner from “Chuck in a Truck” substandard solutions. With a warranty, Chuck will have to come back to do it right. | Completed measure will be warranted for an expected service life of 20 years. | None | Accepted with Modifications | WX provides a one year warranty as specified under Detail Warranty and Service Agreement (2.0702.1) |  | Delete | Delete | Delete
4.1006.1d | Single-Family Homes | Insulation | Attics | Attic Openings | Pull-Down Stairs | Occupant education | A dated receipt signed by the installer will be provided that includes:Coverage areaThicknessR-value | Document job completion to contract specificationsConfirm amount of insulation installedComply with 16 CFR 460.17 | Not Yet Reviewed | 2016-12-16 | 2016-12-16 | Jim Melesky | There are different requirements for installed insulation verses insulation products in the CFR. | For constructed measures a dated receipt signed by the installer will be provided that includes: coverage area thickness and R-value. For commercially available products, the product must have the R-value posted on it. | No cost for this clarification. | Rejected | The SWS does not control manufacturers packaging
4.1006.2a | Single-Family Homes | Insulation | Attics | Attic Openings | Access Doors and Hatches | Installation | Hatches will be insulated to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assemblyAttic hatches rough opening will be surrounded with a durable protective baffle that is higher than the level of the surrounding attic floor insulation | Achieve uniform R-value on the attic door or hatchAchieve uniform R-value on the attic floorPrevent loose attic floor insulation from entering the living area | Not Yet Reviewed | 2017-01-16 | 2017-01-16 | Andrew Long | Need stated minimum insulation or contractors will abuse the opportunity to use R-3 tent kits or R-5 constructed solutions. You can’t have batt insulation for any hatch or other attic access. Batt compresses and loses the R-Value. Too many contractors try to get away on the cheap by using batt. The homeowner deserves better! Same goes for the protective baffle. What do you think will happen to a barrier made of batt? How much loose fill will it hold back once someone leans on the batt? You need wood or rigid foamboard to be a lasting and real protective barrier. Get rid of the batt and make it an effective and lasting measure. | Hatches will be insulated to the same the R-Value of the adjoining insulated assembly with rigid foamboard. If there is limited clearance, it will be insulated to at least R-20. The Hatch rough opening must have a durable protective barrier made or wood or rigid foamboard that is higher than the level of the attic floor insulation. | Yes, a small cost increase. However, said increase results in a significant energy savings for the homeowner and a superior solution to the issue | Accepted with Modifications | Due to the need to maintain flexibility for existing homes (framing, low roof lines, proximity of mechanicals/ electricals), it has been determined that specifying rigid foam in these scenarios may prove limiting and not feasible. AHJs may determine that in order to meet the SWS, rigid foam is chosen, with caveats for clearance issues. |  | No change | Hatches will be insulated to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assembly Attic hatches rough opening will be surrounded with a durable, rigid protective baffle that is higher than the level of the surrounding attic floor insulation | No change
4.1006.2a | Single-Family Homes | Insulation | Attics | Attic Openings | Access Doors and Hatches | Installation | Hatches will be insulated to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assemblyAttic hatches rough opening will be surrounded with a durable protective baffle that is higher than the level of the surrounding attic floor insulation | Achieve uniform R-value on the attic door or hatchAchieve uniform R-value on the attic floorPrevent loose attic floor insulation from entering the living area | Not Yet Reviewed | 2017-01-02 | 2017-01-02 | Jeffrey Shannon | Eliminating the requirement for rigid foamboard is a mistake and should be reversed. There are many ways that the batt insulation can be compressed which will cause the insulating value to fail to meet the max amount structurally available. In most cases and particularly where there is limited space, the batt insulation would most assuredly be compressed during the installation of the measure. I noted the reference of this section to the IECC R402.2.4. This section requires the protective dam to be constructed of wood or equivalent material. The same wording should be used in the SWS. | Hatches will be insulated will be insulated with rigid foamboard to the maximum R-Value structurally allowable up to the R-Value of the adjoining insulated assembly, but in no case less than R-20. Pull-down stair rough opening will be surrounded with a durable dam made or wood or rigid foamboard that is higher than the level of the attic floor insulation. | It is a minimal cost. It is an essential item because without the standard the insulation and dam will not meet the stated requirements. | Accepted with Modifications | Due to the need to maintain flexibility for existing homes (framing, low roof lines, proximity of mechanicals/ electricals), it has been determined that specifying rigid foam in these scenarios may prove limiting and not feasible. AHJs may determine that in order to meet the SWS, rigid foam is chosen, with caveats for clearance issues. |  | No change | Hatches will be insulated to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assembly Attic hatches rough opening will be surrounded with a durable, rigid protective baffle that is higher than the level of the surrounding attic floor insulation | No change
4.1006.2a | Single-Family Homes | Insulation | Attics | Attic Openings | Access Doors and Hatches | Installation | Hatches will be insulated to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assemblyAttic hatches rough opening will be surrounded with a durable protective baffle that is higher than the level of the surrounding attic floor insulation | Achieve uniform R-value on the attic door or hatchAchieve uniform R-value on the attic floorPrevent loose attic floor insulation from entering the living area | Not Yet Reviewed | 2016-12-16 | 2016-12-16 | Jim Melesky | The existing wording of maximum allowable insulation allows for interpretation of contractors to what they might perceive or believe that amount might be, allowing the use of low R-value products and measures. The IECC establishes a minimum R-value of R-30. The insulating material must be non-compressible. This is consistent with the referenced section of the IECC. In addition, the pull-down stair is a doorway from one portion of the structure to another. It must be assumed that this opening will be used over time for maintenance and other purposes. Per the manufacturers' installation instructions for batt insulation, compression of the insulating material will reduce the R-value. When the insulating measure is opened and placed down in the attic, it must be assumed that it will be placed in a position to compress the insulation. That will immediately compromise the R-value and render the measure non-compliant with the requirement. For limited clearance sites, this compression of the insulation is almost an assured incidence even during the installation. Rigid foamboard ensures that the insulating value will be reliable for the expected service life of the measure while the term equivalent material allows for future products with consistent properties required. | Hatches will be insulated to the R-value of the adjoining insulated assembly. In the event of low clearance, the measure will insulated to a minimum of R-30. The insulating material for this measure must be non-compressible, i.e. rigid foamboard or equivalent material. Attic hatches rough opening will be surrounded by a durable dam, made of wood or equivalent dense material that is higher then the level of the attic floor insulation. | There is no cost for clarification of the minimum R-value required. It only eliminates the risk of poor interpretation. Rigid foam is more expensive that batt insulation. However, for this small area, it is a minimal cost. Further, it is essential for the integrity of the overall measure. The measure is only as good as its weakest component. If R-value is important, then the material used must be reliable to provide that stated value. | Accepted with Modifications | Due to the need to maintain flexibility for existing homes (framing, low roof lines, proximity of mechanicals/ electricals), it has been determined that specifying rigid foam in these scenarios may prove limiting and not feasible. AHJs may determine that in order to meet the SWS, rigid foam is chosen, with caveats for clearance issues. |  | No change | Hatches will be insulated to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assembly Attic hatches rough opening will be surrounded with a durable, rigid protective baffle that is higher than the level of the surrounding attic floor insulation | No change
4.1006.2a | Single-Family Homes | Insulation | Attics | Attic Openings | Access Doors and Hatches | Installation | Hatches will be insulated to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assemblyAttic hatches rough opening will be surrounded with a durable protective baffle that is higher than the level of the surrounding attic floor insulation | Achieve uniform R-value on the attic door or hatchAchieve uniform R-value on the attic floorPrevent loose attic floor insulation from entering the living area | Not Yet Reviewed | 2017-01-18 | 2017-01-18 | John Leffler | You can’t give wiggle room on two important insulating issues- 1) The insulating material must be non-compressible, i.e. no batt. Everyone knows that batt will be compressed if used for hatches and the R-Value will be lost. 2) Without a stated minimum, some contractors will use phony clearance problems as an excuse for low R-value solutions. I have seen it in both utility and Wx programs. If you expect a protective barrier to be useful, it can’t be made of batt. It is an old, cheap legacy approach that I thought was finally put to rest. Again, it is a cost cutting way for a contractor, but a bad solution for the customer. R-20 can less than 4 inches of rigid foam-that should fit over any hatch or a person can’t use the ladder. | Hatches will be insulated to the same the R-Value of the adjoining insulated assembly with rigid foamboard. If there is limited clearance, it will be insulated to at least R-20. A durable protective barrier made or wood or rigid foamboard that is higher than the level of the attic floor insulation must be installed around the hatch rough opening. |  | Accepted with Modifications | Due to the need to maintain flexibility for existing homes (framing, low roof lines, proximity of mechanicals/ electricals), it has been determined that specifying rigid foam in these scenarios may prove limiting and not feasible. AHJs may determine that in order to meet the SWS, rigid foam is chosen, with caveats for clearance issues. |  | No change | Hatches will be insulated to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assembly Attic hatches rough opening will be surrounded with a durable, rigid protective baffle that is higher than the level of the surrounding attic floor insulation | No change
4.1006.2a | Single-Family Homes | Insulation | Attics | Attic Openings | Access Doors and Hatches | Installation | Hatches will be insulated to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assemblyAttic hatches rough opening will be surrounded with a durable protective baffle that is higher than the level of the surrounding attic floor insulation | Achieve uniform R-value on the attic door or hatchAchieve uniform R-value on the attic floorPrevent loose attic floor insulation from entering the living area | Not Yet Reviewed | 2017-01-13 | 2017-01-13 | Kyle Seabourn | Batt insulation and other compressible insulations do not hold up for the long term. Anyone who has crawled in an attic knows that. We should not allow the standards to drop just to save a few dollars. When these standards were written in 2009 we got it right. When the standards were dropped we got it wrong. Let’s bring the standards back to where they were. Homeowners are counting on us to do the correct work. | Hatch openings will be insulated with rigid foam or equivalent non-compressible material to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assembly, but no less than R-20. Hatch openings will be surrounded with a durable dam that is higher than the level of the attic floor insulation and constructed of wood, rigid foam board, or other solid material. | The cost increase is very small. The homeowners are worth it | Accepted with Modifications | Due to the need to maintain flexibility for existing homes (framing, low roof lines, proximity of mechanicals/ electricals), it has been determined that specifying rigid foam in these scenarios may prove limiting and not feasible. AHJs may determine that in order to meet the SWS, rigid foam is chosen, with caveats for clearance issues. |  | No change | Hatches will be insulated to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assembly Attic hatches rough opening will be surrounded with a durable, rigid protective baffle that is higher than the level of the surrounding attic floor insulation | No change
4.1006.2a | Single-Family Homes | Insulation | Attics | Attic Openings | Access Doors and Hatches | Installation | Hatches will be insulated to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assemblyAttic hatches rough opening will be surrounded with a durable protective baffle that is higher than the level of the surrounding attic floor insulation | Achieve uniform R-value on the attic door or hatchAchieve uniform R-value on the attic floorPrevent loose attic floor insulation from entering the living area | Not Yet Reviewed | 2016-12-29 | 2016-12-29 | Mike Hight | Removing the requirement for rigid foamboard will result in ineffective measures made of batt insulation. That was a legacy measure that the IECC and the first edition of the SWS rightly eliminated. Batt insulation will compress as soon as a person enters the attic. That will lower the protective dam making it non-compliant with the standard. As soon as the hatch cover is set on the attic floor, the batt insulation will again compress which reduces the R-value. This again makes the R-value non compliant. Where there is limited space, setting the R-value at R-20 seems like a reasonable level and assures an acceptable insulating value. This will protect the resident from very low R-value per-fab kits and constructed batt measures that have been widely used for years that are not consistent with the intent of this section. | Hatches will be insulated to the same the R-Value of the adjoining insulated assembly with rigid foamboard. If there is limited clearance, it will be insulated to a minimum of R-20. Hatch rough opening will be surrounded with a durable protective barrier made or wood, rigid foamboard or equivalent material that is higher than the level of the attic floor insulation. | If you want to meet the standards, you need to use the proper materials. Cost is very small. | Accepted with Modifications | Due to the need to maintain flexibility for existing homes (framing, low roof lines, proximity of mechanicals/ electricals), it has been determined that specifying rigid foam in these scenarios may prove limiting and not feasible. AHJs may determine that in order to meet the SWS, rigid foam is chosen, with caveats for clearance issues. |  | No change | Hatches will be insulated to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assembly Attic hatches rough opening will be surrounded with a durable, rigid protective baffle that is higher than the level of the surrounding attic floor insulation | No change
4.1006.2a | Single-Family Homes | Insulation | Attics | Attic Openings | Access Doors and Hatches | Installation | Hatches will be insulated to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assemblyAttic hatches rough opening will be surrounded with a durable protective baffle that is higher than the level of the surrounding attic floor insulation | Achieve uniform R-value on the attic door or hatchAchieve uniform R-value on the attic floorPrevent loose attic floor insulation from entering the living area | Not Yet Reviewed | 2016-12-16 | 2016-12-16 | RsmithsmithR_1840 | We cannot assume a homeowner will never access the attic after we leave. If the standards do not specifically state that "rigid insulation", batt or other compressible insulation will be often be used. Over time and use the R-value will be compromised and weaken the thermal barrier. Also batt insulation allows air to travel through it. When the conditioned air meets the unconditioned air in this confined space you are creating a breeding ground for mold. This is unsafe for the homeowners we are trying to protect. The rough opening specifically needs a rigid barrier and it must be stated as a "rigid" barrier in the standards. The lack of a rigid barrier allows blown in insulation to easily enter the living space. Without specific language you are leaving room for interpretation. Where there is room for interpretation you will have contractors using it as an opportunity to cut corners. The standards must be changed back to the way they were in 2013. | Hatches will be insulated to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assembly using rigid insulation with a minimum value of R-20. Attic hatches rough opening will be surrounded with a rigid durable protective baffle that is higher than the level of the surrounding attic floor insulation | This change will remove the risk of mold that can occur in this specific area. The cost of rigid foam board is insignificant as it is such a small area. | Accepted with Modifications | Due to the need to maintain flexibility for existing homes (framing, low roof lines, proximity of mechanicals/ electricals), it has been determined that specifying rigid foam in these scenarios may prove limiting and not feasible. AHJs may determine that in order to meet the SWS, rigid foam is chosen, with caveats for clearance issues. |  | No change | Hatches will be insulated to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assembly Attic hatches rough opening will be surrounded with a durable, rigid protective baffle that is higher than the level of the surrounding attic floor insulation | No change
4.1006.2b | Single-Family Homes | Insulation | Attics | Attic Openings | Access Doors and Hatches | Sealing | Access hatch frames will be sealed using caulk, gasket, weatherstrip, or otherwise sealed with an air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary material, suitable film, or solid materialOptions will include installing a latch or lock or frictionally engaged components of a pre-fabricated unit above the opening that do not require a latchThe measure must include a protective baffle or insulation barrier | Prevent air leakage | Not Yet Reviewed | 2016-12-16 | 2016-12-16 | Jim Melesky | The air seal with an expected service life of 20 years are the needed requirements. Stipulating further options limits the use and/or acceptance of equally effective alternative designs. | 2nd sentence should be removed | no cost | Accepted with Modifications | we are not stipulating the exact installation, only giving options |  | No change | Access hatch frames will be sealed using caulk, gasket, weather-strip, or otherwise sealed with an air barrier material, suitable film, or solid material Options include installing a latch, or lock, or frictionally engaged components that do not require a latch The measure must include a protective baffle or insulation barrie | No change
4.1006.2b | Single-Family Homes | Insulation | Attics | Attic Openings | Access Doors and Hatches | Sealing | Access hatch frames will be sealed using caulk, gasket, weatherstrip, or otherwise sealed with an air barrier material, suitable film, or solid material Options will include installing a latch or lock or frictionally engaged components of a pre-fabricated unit above the opening that do not require a latch The measure must include a protective baffle or insulation barrier | Prevent air leakage | Not Yet Reviewed | 2015-11-10 | 2015-11-10 | Pat Beagan | There is confusion from the use of the word "Options" at the start of the 2nd specification. What is SWS intention? Is a latch, lock or frictionally engaged pre fabricated unit above the opening optional or in addition too caulk, weatherstrip, air barrier material, suitable film or solid material? Insulate, dam, seal (and latch?) | There is confusion from the use of the word "Options" at the start of the 2nd specification. What is SWS intention? Is a latch, lock or frictionally engaged pre fabricated unit above the opening optional or in addition too caulk, weatherstrip, air barrier material, suitable film or solid material? Insulate, dam, seal (and latch?) | Yes, the addition of adding a lock, latch or pre fabricated unit to the insulation dam and sealing of the access hatch will increase the cost. | Accepted with Modifications | Modified for clarification |  | No change | Access hatch frames will be sealed using caulk, gasket, weather-strip, or otherwise sealed with an air barrier material, suitable film, or solid material Options include installing a latch, or lock, or frictionally engaged components that do not require a latch The measure must include a protective baffle or insulation barrier | No change
4.1006.2b | Single-Family Homes | Insulation | Attics | Attic Openings | Access Doors and Hatches | Sealing | Access hatch frames will be sealed using caulk, gasket, weatherstrip, or otherwise sealed with an air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary material, suitable film, or solid materialOptions will include installing a latch or lock or frictionally engaged components of a pre-fabricated unit above the opening that do not require a latchThe measure must include a protective baffle or insulation barrier | Prevent air leakage | Not Yet Reviewed | 2016-12-16 | 2016-12-16 | RsmithsmithR_1840 | The measures we have built are heavy enough that the weatherstripping is compressed and an air seal is formed. There is no need to make latches or hook and eye mandatory | Options may include installing a latch or lock or frictionally engaged components of a pre-fabricated unit above the opening that do not require a latch | No. Removing the latch and hook and eye section will make this measure less expensive. | Accepted with Modifications | Modified for clarification |  | No change | Access hatch frames will be sealed using caulk, gasket, weather-strip, or otherwise sealed with an air barrier material, suitable film, or solid material Options include installing a latch, or lock, or frictionally engaged components that do not require a latch The measure must include a protective baffle or insulation barrie | No change
4.1006.2c | Single-Family Homes | Insulation | Attics | Attic Openings | Access Doors and Hatches | Attachment | Insulation will be permanently attached and in complete contact with the air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary | Insulate to prescribed R-value | Not Yet Reviewed | 2017-01-16 | 2017-01-16 | Andrew Long | There is a pre-fab kit that I have installed that meets all of the SWS requirements except the insulation is installed on the top of the protective barrier. The current wording limits the design of alternate and equally effective measures. | Insulation will be permanently attached above the hatch. The insulation is attached in a manner that allows entry through the hatch into the attic and closes to re-establish the insulating value. | A slight initial increase in cost, however that cost is recouped by the homeowner in reduced energy costs over a very short period of time | Rejected | the current SWS langauge does not prohibit the installation described in the comment
4.1006.2c | Single-Family Homes | Insulation | Attics | Attic Openings | Access Doors and Hatches | Attachment | Insulation will be permanently attached and in complete contact with the air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary | Insulate to prescribed R-value | Not Yet Reviewed | 2016-12-16 | 2016-12-16 | Jim Melesky | Making the insulation attached and in complete contact with the air barrier limits designs that are alternative to the common method of attaching insulation to the attic side of the hatch cover. The requirements of insulating value, air seal and expected service life remain constant. | Insulation will be permanently installed over the hatch. | No | Rejected | the current SWS langauge does not prohibit the installation described in the comment
4.1006.2d | Single-Family Homes | Insulation | Attics | Attic Openings | Access Doors and Hatches | Durability | Completed measure will meet a minimum expected service life of 20 years | Ensure a minimum expected service life | Not Yet Reviewed | 2017-01-16 | 2017-01-16 | Andrew Long | Without a warranty or contractor guaranty, the very important service life will not be a real requirement. | Completed measure will meet a minimum expected service life of 20 years, backed by a manufacturer’s warranty or contractor guaranty. | There is no increase to cost for the homeowner by addition of a guarantee/warranty. | Accepted with Modifications | WX provides a one year warranty as specified under Detail Warranty and Service Agreement (2.0702.1) |  | Delete | Delete | Delete
4.1006.2d | Single-Family Homes | Insulation | Attics | Attic Openings | Access Doors and Hatches | Durability | Completed measure will meet a minimum expected service life of 20 years | Ensure a minimum expected service life | Not Yet Reviewed | 2017-01-02 | 2017-01-02 | Jeffrey Shannon | Without a warranty, the durability to last 20 years will have no means of confidence which also makes it a subjective quality. Requiring a warranty assures consistent quality. As a contractor, it establishes a level playing field when we compete against low quality contractors. | Completed measure will be warranted for a minimum of 20 years | No cost if the measure meets the standards. | Accepted with Modifications | WX provides a one year warranty as specified under Detail Warranty and Service Agreement (2.0702.1) |  | Delete | Delete | Delete
4.1006.2e | Single-Family Homes | Insulation | Attics | Attic Openings | Access Doors and Hatches | Occupant education | A dated receipt signed by the installer will be provided that includes:Coverage areaThicknessR-value | Document job completion to contract specificationsConfirm amount of insulation installedComply with 16 CFR 460.17 | Not Yet Reviewed | 2016-12-16 | 2016-12-16 | Jim Melesky | this is prescribed by the FTC CFR Title 16, part 460 as well as the IECC | For on site constructed measures, a dated receipt signed by the installer will be provided that includes: coverage area, thickness and R-Value For commercially available products, the product must state the R-Value of the installed product. | no | Rejected | The SWS does not control manufacturers packaging
4.1006.2e | Single-Family Homes | Insulation | Attics | Attic Openings | Access Doors and Hatches | Occupant education | A dated receipt signed by the installer will be provided that includes:Coverage areaThicknessR-value | Document job completion to contract specificationsConfirm amount of insulation installedComply with 16 CFR 460.17 | Not Yet Reviewed | 2017-01-16 | 2017-01-16 | State of Alaska... | Eliminate redundancy. | Why is this necessary? It seems that we are overdocementing, requiring too much in the field files |  | Rejected | The SWS follows 16 CFR 460.17 regulation
4.1101.1a | Single-Family Homes | Insulation | Walls | Preparation | Exterior Wall Dense Packing | Preparation | Lead and asbestos safety procedures will be followedCavities will be free of hazards, intact, and able to support dense pack Dense pack The process of installing loose-fill insulation to reduce air flow and perform to a stated R-value pressuresDrilling hazards (e.g., wiring, venting, fuel piping) will be locatedBlocking will be installed around:All openings to inside crawl space and basement for fibrous materialHigh temperature fire-rated materialsWiring and electrical hazardsHeat sourcesAccess to exterior wall cavities will be gained, sheathing will be drilled as needed and probed to locate each cavity, wall studs, and blockersInterior will be masked and dust controlled during drilling when accessing from interiorElectricity supply will be confirmed and will support blowing machine power demandBlowing machine pressure test will be performed with air on full, feed off, agitator running, and gate closedHose outlet pressure will be at least 80 IWC IWC Inches of water column or 2.9 psi Psi Pounds per square inch for cellulose insulation; for other types of dense pack Dense pack The process of installing loose-fill insulation to reduce air flow and perform to a stated R-value insulation, check manufacturer specification for blowing machine set up | Prevent damage to houseProvide a clean work spaceProvide thorough access to allow 100% coverageEnsure proper equipment and process results in consistent densityPrevent settling and retard air flow through cavitiesProtect worker and occupant health | Rejected | 2014-06-19 | 2014-06-24 | Stephen Lommele | Test comment. |  |  | Rejected | test comment
4.1103.1a | Single-Family Homes | Insulation | Walls | Enclosed Walls | Dense Pack Exterior Walls | Exterior dense pack Dense pack The process of installing loose-fill insulation to reduce air flow and perform to a stated R-value | Using fill tube, 100% of each cavity will be filled to a consistent density:Cellulose insulation used in an enclosed cavity will be installed at 3.5 pounds per cubic foot or greater densityBlown fiberglass, mineral fiber, or rock and slag wool used in an enclosed cavity will be installed at or above the manufacturer recommended density to limit air flow that corresponds to an air permeance value of 3.5 cfm CFM Cubic feet per minute /sq. ft. at 50 pascals, as measured using BPI BPI Building Performance Institute, www.bpi.org -102 "Standard for Air Resistance of Thermal Insulation Used in Retrofit Cavity Applications – Material Specification" or ASTM ASTM ASTM International, www.astm.org C 522, E 283, or E 2178; the number of bags installed will be confirmed and will match the number required on the coverage chartInsulation will be verified to prevent visible air movement using chemical smoke at 50 pascals of pressure difference | Eliminate voids and settlingMinimize framing cavity air flows | Not Yet Reviewed | 2017-01-12 | 2017-01-12 | Joel Harms | 3.5 pounds per cubic foot or greater density can be achieved without the use of a fill tube. Several would-be contractors have refused to work for the weatherization program on the grounds that their installation methods are equivalent in result to the fill tube method. This has been verified with mock walls that were constructed to test the differing installation methods and comparing the weights of insulation subsequently removed from the test wall cavities. The outcome of the tests served to defend the alternate method as equally effective. As a result of DOE dictating the particular method of installation as well as the resulting outcome, a competitive procurement process for installing contractors has been lost in our region. | Delete words, "Using fill tube". | No. In fact it will provide us an opportunity to have more competition among prospective installers which may well lower the costs of providing side wall insulation services. | Accepted with Modifications | spec rewritten to compromise with commenter |  | No change | Using fill tube or an alternative method as approved by the authority having jurisdiction, 100% of each cavity will be filled to a consistent density: Cellulose insulation used in an enclosed cavity will be installed at 3.5 pounds per cubic foot or greater density Blown fiberglass, mineral fiber, or rock and slag wool used in an enclosed cavity will be installed at or above the manufacturer recommended density to limit air flow that corresponds to an air permeance value of 3.5 cfm /sq. ft. at 50 pascals, as measured using BPI -102 "Standard for Air Resistance of Thermal Insulation Used in Retrofit Cavity Applications – Material Specification" or ASTM C 522, E 283, or E 2178; the number of bags installed will be confirmed and will match the number required on the coverage chart All holes and penetrations will be plugged and/or sealed Insulation will be verified to prevent visible air movement using chemical smoke at 50 pascals of pressure difference | No change
4.1103.2c | Single-Family Homes | Insulation | Walls | Enclosed Walls | Additional Exterior Wall Cavities | Dense packing | Using fill tube, 100% of each cavity will be filled to a consistent density: Cellulose insulation used in an enclosed cavity will be installed at 3.5 pounds per cubic foot or greater densityBlown fiberglass, mineral fiber, or rock and slag wool used in an enclosed cavity will be installed at or above the manufacturer recommended density to limit airflow that corresponds to an air permeance value of 3.5 cfm CFM Cubic feet per minute /sq. ft. at 50 pascals, as measured using BPI BPI Building Performance Institute, www.bpi.org -102 "Standard for Air Resistance of Thermal Insulation Used in Retrofit Cavity Applications—Material Specification" or ASTM ASTM ASTM International, www.astm.org C 522, E 283, or E 2178; the number of bags installed will be confirmed and will match the number required on the coverage chart Insulation will be verified to prevent visible air movement using chemical smoke at 50 pascals of pressure difference | Eliminate voids and settlingMinimize framing cavity air flows | Not Yet Reviewed | 2017-01-16 | 2017-01-16 | State of Alaska... | Consistency with other specs | Specification(s): Insulation will be verified to prevent visible air movement at 50 pascals of pressure difference using chemical smoke, IR scans, or other approved verification method. |  | Accepted with Modifications | Modified to include AHJ langauage |  | No change | Using fill tube, 100% of each cavity will be filled to a consistent density: Cellulose insulation used in an enclosed cavity will be installed at 3.5 pounds per cubic foot or greater density Blown fiberglass, mineral fiber, or rock and slag wool used in an enclosed cavity will be installed at or above the manufacturer recommended density to limit airflow that corresponds to an air permeance value of 3.5 cfm /sq. ft. at 50 pascals, as measured using BPI, SITE -102 "Standard for Air Resistance of Thermal Insulation Used in Retrofit Cavity Applications—Material Specification" or ASTM SITE C 522, E 283, or E 2178; the number of bags installed will be confirmed and will match the number required on the coverage chart Insulation will be verified to prevent visible air movement at 50 pascals of pressure difference using chemical smoke or other approved verification method by the authority having jurisdiction | No change
4.1103.4f | Multifamily Homes | Insulation | Walls | Enclosed Walls | Dense Packing Blown Insulation | Exterior dense pack Dense pack The process of installing loose-fill insulation to reduce air flow and perform to a stated R-value | Using fill tube, 100% of each cavity will be completely filled to a consistent density:Cellulose insulation used in an enclosed cavity will be installed at 3.5 pounds per cubic foot or greater densityBlown fiberglass, mineral fiber, rock and slag wool, or spray foam used in an enclosed cavity will be installed in accordance at or above manufacturer recommended density to limit air flow that corresponds to an air permeance value of 3.5 cubic feet per minute/square feet at 50 pascals, as measured using the following applicable methods: BPI BPI Building Performance Institute, www.bpi.org -102 Standard for Air Resistance of Thermal Insulation Used in Retrofit Cavity Applications, orMaterial Specification, or ASTM ASTM ASTM International, www.astm.org C 522, or ASTM ASTM ASTM International, www.astm.org E 283, or ASTM ASTM ASTM International, www.astm.org E 2178All insulation materials used will meet ASTM ASTM ASTM International, www.astm.org E84 flame spread/smoke development rating of 25/50The number of bags installed will be confirmed and will match the number required on the coverage chart Insulation will be verified to prevent visible air movement using chemical smoke at 50 pascals of pressure difference | Eliminate voids and settlingMinimize framing cavity air flow | Not Yet Reviewed | 2017-01-18 | 2017-01-18 | Jonathan Ballew | The would align the verification method of this detail with 4.1003.2a | "insulation will be verified using IR scan, chemical smoke, or other approved verification method" | no | Accepted | Align similar SWS specifications |  | No change | Using fill tube, 100% of each cavity will be completely filled to a consistent density: Cellulose insulation used in an enclosed cavity will be installed at 3.5 pounds per cubic foot or greater density Blown fiberglass, mineral fiber, rock and slag wool, or spray foam used in an enclosed cavity will be installed in accordance at or above manufacturer recommended density to limit air flow that corresponds to an air permeance value of 3.5 cubic feet per minute/square feet at 50 pascals, as measured using the following applicable methods: BPI -102 Standard for Air Resistance of Thermal Insulation Used in Retrofit Cavity Applications, or Material Specification, or ASTM C 522, or ASTM E 283, or ASTM E 2178 All insulation materials used will meet ASTM E84 flame spread/smoke development rating of 25/50 The number of bags installed will be confirmed and will match the number required on the coverage chart Insulation will be verified to prevent visible air movement at 50 pascals of pressure difference using chemical smoke or other approved verification method by the authority having jurisdiction | No change
4.1402.1a | Single-Family Homes | Insulation | Basements and Crawl Spaces | Basements and Crawl Space Walls | Closed Crawl Spaces—Wall Insulation | Insulation selection | A non fibrous, fire-rated Class I insulation will be used with a minimum life expectancy of 10 years | Provide fire-safe durable insulation | Not Yet Reviewed | 2017-01-18 | 2017-01-18 | Jonathan Ballew | This will ensure that the installed insulation will meet its design life without premature failure. Additionally, this will ensure good indoor air quality in the crawlspace. | add, "Non-fibrous insulation must e used if there is any moisture present or signs of past moisture intrusion present in the crawlspace" | It is possible that there could be an increase in cost. However, the addition of this provision will serve to protect the indoor air quality in the building. Additionally, this will help to align this detail with the insulate basement walls - moisture present detail. | Rejected | The SWS stipulates the minimum, programs are allowed to provide additional requirements. There are fibrous solutions that comply with the commenters problem. This could add undue costs.
5.3001.1a | Single-Family Homes | Heating and Cooling | Forced Air | Design | Load Calculation and Equipment Selection | Load calculation | Load calculation will be performed in accordance with ANSI ANSI American National Standards Institute, www.ansi.org / ACCA ACCA Air Conditioning Contractors of America, www.acca.org 2 Manual J-2011 (Residential Load Calculation) and manufacturer specifications | Properly size equipment for load | Not Yet Reviewed | 2017-01-19 | 2017-01-19 | bryan burris | Add section for Man. J requirement to Manufactured Homes Specifications. | ***For Manufactured Homes*** Load calculation will be performed in accordance with ANSI/ACCA 2 Manual J-2011 (Residential Load Calculation) and manufacturer specifications |  | Accepted with Modifications | New tab for "Manufactured Housing" will be added, and the Detail in its entirety will match "Single-Family Homes" word for word. |  | No change | No change | No change
5.3001.1a | Single-Family Homes | Heating and Cooling | Forced Air | Design | Load Calculation and Equipment Selection | Load calculation | Load calculation will be performed in accordance with ANSI ANSI American National Standards Institute, www.ansi.org / ACCA ACCA Air Conditioning Contractors of America, www.acca.org 2 Manual J-2011 (Residential Load Calculation) and manufacturer specifications | Properly size equipment for load | Not Yet Reviewed | 2017-01-18 | 2017-01-18 | Glen Salas Salas | Accurate, optimal load calculations are accurate, optimal load calculations for a well functioning system, whether or not it's a single family or manufactured home. I suspect leaving off the requirements for manufactured homes was an oversight. | This entire 5.3001.1 section is written only for Single Family homes. It (and probably 5.3001.2) should also apply (with whatever changes the review committee agrees upon) for Manufactured homes. | Well, this is best practice, so everyone should be doing it anyway. This comment is for clarification. | Accepted with Modifications | New tab for "Manufactured Housing" will be added, and the Detail in its entirety will match "Single-Family Homes" word for word. Apply the previous statement to Detail 5.3001.2 as well |  | No change | No change | No change
5.3002.13b | Multifamily Homes | Heating and Cooling | Forced Air | Site Preparation | Preparation for New Equipment&mdash;Mid and High Rise | Environmental hazards | If mold and/or asbestos-like substance is found to be present, it must be tested by a certified organization, and all system components and possible disturbed surrounding areas will be certified free of asbestos and/or mold by a licensed professional before equipment removal can begin | Protect workers and occupants from injury | Not Yet Reviewed | 2017-01-20 | 2017-01-20 | Kelly Cutchin C... | If it's in good shape and won't be disturbed, it seems like an added expense. | Asbestos only needs to be tested if it is friable and/or will be disturbed during the work. | No | Accepted | Leaving asbestos undisturbed is the proper procedure, unless there is a friable suspected asbestos containing material in an area that will be disturbed by work, in which case it must be tested and remediated if necessary. However, if mold is identified, it must be removed, regardless of whether or not it is in an area that will be disturbed by work. |  | No change | If mold covering more than 3 square feet is found to be present, it must be tested by a certified organization, and all system components and possible disturbed surrounding areas will be certified free of mold by a licensed professional before equipment removal can begin. If a friable asbestos-like substance is found to be present in an area that will be disturbed by work, it must be tested by a certified organization, and all system components and possible disturbed surrounding areas will be certified free of asbestos by a licensed professional before equipment removal can begin | No change
5.3002.4b | Multifamily Homes | Heating and Cooling | Forced Air | Site Preparation | Preparation for New Equipment&mdash;Low Rise | Environmental hazards | If mold and/or asbestos-like substance is found to be present, it must be tested by a certified organization, and all system components and possible disturbed surrounding areas must be certified free of asbestos and/or mold by a licensed professional before equipment removal can begin | Protect workers and occupants from injury | Not Yet Reviewed | 2017-01-20 | 2017-01-20 | Kelly Cutchin C... | If it's in good shape and won't be disturbed, it seems like an added expense. | Asbestos should only need to be tested if it is friable and/or will be disturbed by the work being conducted. | No | Accepted | Leaving asbestos undisturbed is the proper procedure, unless there is a friable suspected asbestos containing material in an area that will be disturbed by work, in which case it must be tested and remediated if necessary. However, if mold is identified, it must be removed, regardless of whether or not it is in an area that will be disturbed by work. |  | No change | If mold covering more than 3 square feet is found to be present, it must be tested by a certified organization, and all system components and possible disturbed surrounding areas will be certified free of mold by a licensed professional before equipment removal can begin. If a friable asbestos-like substance is found to be present in an area that will be disturbed by work, it must be tested by a certified organization, and all system components and possible disturbed surrounding areas will be certified free of asbestos by a licensed professional before equipment removal can begin | No change
5.3003.14a | Single-Family Homes, Manufactured Housing | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Gas-Fired Appliances (LP and Natural Gas) | Place appliance in operation | Heating equipment will be placed in operation in accordance with applicable NFPA NFPA National Fire Protection Association, www.nfpa.org standards and manufacturer specifications when available | Ensure equipment: Operates as designed Operates safely Operates efficiently Is durable | Not Yet Reviewed | 2017-01-18 | 2017-01-18 | Glen Salas Salas | SSE measurement is important for an energy audit. The SSE measurement requirement is included for oil-fired furnaces and I suspect it was an oversight to leabe it out for gas-fired. | Somewhere in 5.3003.14 it should state specifically that steady state efficiency should be measured. | No, this section already requires measurements of excess air, CO2, O2 and CO. If you've measured all of those then any metering you've used will give you SSE. | Accepted | SSE operation is called for in the forced air section. The language should be the same. Detail 5.3003.14 will have new spec added (number TBD) regarding SSE. Language for SSE will follow specs 5.3003.15e / 5.3003.2c.
5.3003.14d | Single-Family Homes, Manufactured Housing | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Gas-Fired Appliances (LP and Natural Gas) | Excess combustion air | Excess combustion air will be calculated and verified in accordance with industry manuals (e.g., Testo, Bacharach) | Ensure equipment: Operates as designed Operates safely Operates efficiently Is durable | Not Yet Reviewed | 2017-01-16 | 2017-01-16 | State of Alaska... | Not necessary if co and efficiency are ok | Not usually required |  | Accepted | Excess combustion air does not need to be tested if CO and efficiency are acceptable. This Specification (row) will be deleted. The entire detail was re-ordered to better align with similar details within the SWS. Embedded Word document shows changes to 5.3003.14. |  | Delete row | Delete row | Delete row
5.3003.14e | Single-Family Homes, Manufactured Housing | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Gas-Fired Appliances (LP and Natural Gas) | Carbon monoxide ( CO CO Carbon monoxide ) in flue gas | CO CO Carbon monoxide in the undiluted flue gas will be less than 100 ppm | Ensure equipment: Operates as designed Operates safely Operates efficiently Is durable | Not Yet Reviewed | 2016-12-09 | 2016-12-09 | Kelly Cutchin C... | Aligning SWS with accepted industry standards. | CO action levels should be updated to align with BPI 1200 - 200 ppm as measured and 400 ppm air-free. Do for MH and SF versions. | No | Accepted | Align with BPI-1200 as has been done with other Details in the SWS. |  | No change | CO in the undiluted flue gas will be less than 400 ppm air-free | No change
5.3003.14e | Single-Family Homes, Manufactured Housing | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Gas-Fired Appliances (LP and Natural Gas) | Carbon monoxide ( CO CO Carbon monoxide ) in flue gas | CO CO Carbon monoxide in the undiluted flue gas will be less than 100 ppm | Ensure equipment: Operates as designed Operates safely Operates efficiently Is durable | Not Yet Reviewed | 2017-01-16 | 2017-01-16 | State of Alaska... | Seems that there is inconsistency between natural and airfree testing for co, most technicians are familiar with the natural tests not airfree | Inconsistency |  | Rejected | Aligning the SWS with BPI-1200 and ACCA 12QH. The inconsistency lies within the referenced standards.
5.3003.14f | Single-Family Homes, Manufactured Housing | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Gas-Fired Appliances (LP and Natural Gas) | Testing/inspection holes | All testing and inspection holes will be sealed with manufacturer approved materials | Ensure equipment: Operates as designed Operates safely Operates efficiently Is durable | Not Yet Reviewed | 2017-01-20 | 2017-01-20 | State of Alaska... | not aware of what are approved materials | what are approved materials? |  | Accepted with Modifications | All test and inspection holed must be sealed as approved by the authority having jurisdiction |  | No change | All testing and inspection holes will be sealed as approved by the authority having jurisdiction (ed: Also appply to 5.3003.15j) | No change
5.3003.15b | Manufactured Housing | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Oil-Fired Appliances | Oil system: nozzle | Nozzle size, angle, and spray pattern will be correct for design input and within equipment firing rate of the heating system manufacturer | Ensure equipment: Operates as designed Operates safely Operates efficiently Is durable | Not Yet Reviewed | 2017-01-16 | 2017-01-16 | State of Alaska... | We often dont have this information and this requires more technical expertise. Efficiency and co testing should be adequate | Not valid test |  | Accepted with Modifications | As a result of several comments, Detail 5.3003.15 has been eliminated. The content has moved to Detail 5.3003.2: Combustion Analysis of Oil-Fired Appliances, under the tab for Manufactured Housing. This was done because the Detail for the two housing types are so similar. Also, the Detail has been heavily edited. This includes rearranging Specifications (rows), adding one or more Specifications, and clarifying language. Embedded Word document shows changes to 5.3003. |  | Delete Spec | Delete Spec | Delete Spec
5.3003.1a | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Data Plate Verification | Data plate verification | Equipment will be visually inspectedInformation will be recorded from the equipment data plates indoors and outdoors | Ensure technician has equipment data necessary for commissioning and future service work | Not Yet Reviewed | 2017-01-20 | 2017-01-20 | Bruce Hagen | Data plates and other information not always available on older systems. | Information will be recorded from the equipment data plates indoors and outdoors where available | No | Accepted | Name plates are not always available on older systems. Information will be recorded from name plates where it is available. |  | No change | Equipment will be visually inspected Information will be recorded from the equipment data plates indoors and outdoors where available | No change
5.3003.2a | [12 empty] | per exec committee |  |  | Accepted | As a result of several comments, Detail 5.3003.2 has been heavily edited. This includes rearranging Specifications (rows), adding one or more Specifications, and clarifying language. Also, because the single family and manufactured housing version of this Detail are so similar, the manufactured housing version (Detail 5.3003.15: Combustion Analysis of Oil-Fired Appliances) has been eliminated and the content has been added as a tab to Detail 5.3003.2. To see a redlined version of Detail 5.3003.2 comparing the old version with the new version, click on this embedded document. |  | Oil System: filter | Filter will be present, clean, and leak free | Ensure oil filter is present and functional.
5.3003.2a | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Oil-Fired Appliances | Oil system: nozzle size | Nozzle size will be correct for design input and within equipment firing rate of the heating system manufacturer | Ensure equipment operates as designed Ensure equipment operates safely Ensure equipment operates efficientlyEnsure equipment is durable | Not Yet Reviewed | 2017-01-20 | 2017-01-20 | Bruce Hagen | Often no information available. | Nozzle size, angle, and spray pattern will be correct for design input and within equipment firing rate of the heating system manufacturer. Position of nozzle and electrodes will be in accordance with manufacturer specifications. When no manufacturers information is available the technician will have to rely on other tests to ensure proper operation of the system. | No | Accepted with Modifications | As a result of several comments, Detail 5.3003.2 has been heavily edited. This includes rearranging Specifications (rows), adding one or more Specifications, and clarifying language. Also, because the single family and manufactured housing version of this Detail are so similar, the manufactured housing version (Detail 5.3003.15: Combustion Analysis of Oil-Fired Appliances) has been eliminated and the content has been added as a tab to Detail 5.3003.2. To see a redlined version of Detail 5.3003.2 comparing the old version with the new version, click on this embedded document. Embedd Word doc 5.3003
5.3003.2a | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Oil-Fired Appliances | Oil system: nozzle size | Nozzle size will be correct for design input and within equipment firing rate of the heating system manufacturer | Ensure equipment operates as designed Ensure equipment operates safely Ensure equipment operates efficientlyEnsure equipment is durable | Not Yet Reviewed | 2017-01-16 | 2017-01-16 | State of Alaska... | Most wx field technicians are not qualified to test for fuel pressure or easily verify correct nozzle size. These are tests performed by a heating technician | nozzle size and fuel pressure test should not be required |  | Accepted with Modifications | As a result of several comments, Detail 5.3003.2 has been heavily edited. This includes rearranging Specifications (rows), adding one or more Specifications, and clarifying language. Also, because the single family and manufactured housing version of this Detail are so similar, the manufactured housing version (Detail 5.3003.15: Combustion Analysis of Oil-Fired Appliances) has been eliminated and the content has been added as a tab to Detail 5.3003.2. To see a redlined version of Detail 5.3003.2 comparing the old version with the new version, click on this embedded document.
5.3003.2a | [15 empty] | Accepted with Modifications | As a result of several comments, Detail 5.3003.2 has been heavily edited. This includes rearranging Specifications (rows), adding one or more Specifications, and clarifying language. Also, because the single family and manufactured housing version of this Detail are so similar, the manufactured housing version (Detail 5.3003.15: Combustion Analysis of Oil-Fired Appliances) has been eliminated and the content has been added as a tab to Detail 5.3003.2. To see a redlined version of Detail 5.3003.2 comparing the old version with the new version, click on this embedded document. | 5.3003.2b | Nozzle | Nozzle size, angle, and spray pattern will be correct for design input and within equipment firing rate of the heating system manufacturer. Position of nozzle and electrodes will be in accordance with manufacturer specifications | Ensure equipment is outfitted with the correct nozzle per manufacturer guidelines.
5.3003.2c | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Oil-Fired Appliances | Oil system: steady state efficiency ( SSE SSE Steady state efficiency ) | Measurement will be verified in accordance with manufacturer specifications | Ensure equipment operates as designed Ensure equipment operates safely Ensure equipment operates efficientlyEnsure equipment is durable | Not Yet Reviewed | 2017-01-18 | 2017-01-18 | Glen Salas Salas | Accurate assessment of HVAC efficiency is essential to a good audit whether or not it's a single family or manufactured home. I suspect leaving off the requirements for manufactured homes was an oversight. | This should also apply to manufactured homes, not just single family. I suspect leaving off the requirements for manufactured homes was an oversight. | This is best practice so presumably all good assessors do it anyway. This change is just a clarification for the sloppy assessors. | Accepted with Modifications | As a result of several comments, Detail 5.3003.2 has been heavily edited. This includes rearranging Specifications (rows), adding one or more Specifications, and clarifying language. Also, because the single family and manufactured housing version of this Detail are so similar, the manufactured housing version (Detail 5.3003.15: Combustion Analysis of Oil-Fired Appliances) has been eliminated and the content has been added as a tab to Detail 5.3003.2. To see a redlined version of Detail 5.3003.2 comparing the old version with the new version, click on this embedded document. CK: Embedd Word doc 5.3003
5.3003.2g | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Oil-Fired Appliances | Excess air | Excess air will be calculated and shown to be in accordance with manufacturer specifications | Ensure equipment operates as designed Ensure equipment operates safely Ensure equipment operates efficientlyEnsure equipment is durable | Not Yet Reviewed | 2017-01-20 | 2017-01-20 | State of Alaska... | This seems to be a more extensive test then most weatherization field technicians would perform. Also with the age of most heating systems in retrofit work, the manufactures specs aren't necessarily available. | If manufactured specifications is available for heating unit, excess air will be calculated and shown to be in accordance | Yes, more training and cost if a hvac contractor needs to be used. | Accepted with Modifications | As a result of several comments, Detail 5.3003.2 has been heavily edited. This includes rearranging Specifications (rows), adding one or more Specifications, and clarifying language. Also, because the single family and manufactured housing version of this Detail are so similar, the manufactured housing version (Detail 5.3003.15: Combustion Analysis of Oil-Fired Appliances) has been eliminated and the content has been added as a tab to Detail 5.3003.2. To see a redlined version of Detail 5.3003.2 comparing the old version with the new version, click on this embedded document. Embedd Word doc 5.3003
5.3003.3b | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Evaluating Air Flow | External static pressure | External static pressure will be in accordance with manufacturer specifications | Ensure equipment operates as designed Ensure equipment operates efficiently Ensure equipment provides comfort Ensure equipment operates safely Ensure equipment is durable | Not Yet Reviewed | 2017-01-16 | 2017-01-16 | State of Alaska... | Additional test not usually done | Do not need additional test temperature rise is enough | More training more tests | Rejected | External static pressure is important for air conditioning applications. Temperature rise does not pick up static pressure measurement.
5.3003.3b | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Evaluating Air Flow | External static pressure | External static pressure will be in accordance with manufacturer specifications | Ensure equipment operates as designed Ensure equipment operates efficiently Ensure equipment provides comfort Ensure equipment operates safely Ensure equipment is durable | Not Yet Reviewed | 2017-01-16 | 2017-01-16 | State of Alaska... | Additional test not usually done | Do not need additional test temperature rise is enough | More training more tests | Rejected | External static pressure is important for air conditioning applications. Temperature rise does not pick up static pressure measurement.
5.3003.3d | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Evaluating Air Flow | Pressure drop: filter | Pressure drop across filter will be in accordance with manufacturer specifications | Ensure equipment operates as designed Ensure equipment operates efficiently Ensure equipment provides comfort Ensure equipment operates safely Ensure equipment is durable | Not Yet Reviewed | 2017-01-16 | 2017-01-16 | State of Alaska... | More testing beyond the usual test for most field technicians | This has been a visual test to see if filter is needing replacement | This adds training costs or heating contractors | Accepted | If total system air flow is being checked, no additional test required. Changing Specification Title to Filter Inspection (user will verify that correct type is installed and that it is clean) |  | Filter Inspection | Visual inspection to verify filter type is per manufacturer specifications, and is clean | No change
5.3003.3e | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Evaluating Air Flow | Balancing room flow: new ductwork | Air flow will be measured at each register to ensure proper air flow delivery | Ensure equipment operates as designed Ensure equipment operates efficientlyEnsure equipment provides comfort Ensure equipment operates safely Ensure equipment is durable | Not Yet Reviewed | 2017-01-20 | 2017-01-20 | Kelly Cutchin C... | There are alternate, equally effective approaches we should let people continue to use. | Proper air flow delivery to each room will be ensured by one of the following: Measuring air flow at each register to ensure proper air flow delivery, or Measuring heat rise, room pressures, and interviewing residents to ensure their comfort. | No | Accepted | Offer alternative pathways to ensure proper air flow delivery to each room |  | No change | Proper air flow delivery to each room will be ensured by one of the following: Measuring air flow at each register OR Measuring heat rise, room pressures, and interviewing residents to ensure their comfort. | No change
5.3003.3e | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Evaluating Air Flow | Balancing room flow: new ductwork | Air flow will be measured at each register to ensure proper air flow delivery | Ensure equipment operates as designed Ensure equipment operates efficientlyEnsure equipment provides comfort Ensure equipment operates safely Ensure equipment is durable | Not Yet Reviewed | 2017-01-16 | 2017-01-16 | State of Alaska... | This is usually a visual tactile inspection to see that adequate heat or coooling is being distributed.. Is there a standard airflow? | Inspect registers for good adequate airflow | This will require more training and equipment | Rejected | This Specification is being revised in response to other comments CK: Not sure what is going on here.
5.3003.3f | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Evaluating Air Flow | Supply wet bulb and dry bulb | Supply wet bulb and dry bulb air temperatures will be recorded | Ensure equipment operates as designed Ensure equipment operates efficiently Ensure equipment provides comfort Ensure equipment operates safely Ensure equipment is durable | Not Yet Reviewed | 2017-01-20 | 2017-01-20 | Kelly Cutchin C... | Climate-appropriateness | Rewrite the objectives, these are repeated for every row of this SWS. Consider rephrasing specification - in non-cooling climates, is the wet bulb temperature useful? If not, remove or rephrase to make it climate-appropriate. | No | Accepted with Modifications | Wet bulb temperature measurement is for cooling systems only |  | Supply and return temperature measurements | Supply and return wet bulb (wet bulb temperature is measured for cooling systems only) and dry bulb air temperatures will be recorded | No change
5.3003.3f | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Evaluating Air Flow | Supply wet bulb and dry bulb | Supply wet bulb and dry bulb air temperatures will be recorded | Ensure equipment operates as designed Ensure equipment operates efficiently Ensure equipment provides comfort Ensure equipment operates safely Ensure equipment is durable | Not Yet Reviewed | 2017-01-16 | 2017-01-16 | State of Alaska... | Beyond most technicians ability | This tests is not needed. | Yes more equipment and training | Accepted with Modifications | Wet bulb temperature measurement is for cooling systems only |  | Supply and return temperature measurements | Supply and return wet bulb (wet bulb temperature is measured for cooling systems only) and dry bulb air temperatures will be recorded | No change
5.3003.3g | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Evaluating Air Flow | Return wet bulb and dry bulb | Return wet bulb and dry bulb air temperatures will be recorded | Ensure equipment operates as designed Ensure equipment operates efficiently Ensure equipment provides comfort Ensure equipment operates safely Ensure equipment is durable | Not Yet Reviewed | 2017-01-20 | 2017-01-20 | Kelly Cutchin C... | Climate appropriateness | Rewrite the objectives, these are repeated for every row of this SWS. Consider rephrasing specification - in non-cooling climates, is the wet bulb temperature useful? If not, remove or rephrase to make it climate-appropriate. | No | Accepted with Modifications | Combining 5.3003.3f with 5.3003.3g (eliminate Specification row g). Rewritten for clarity |  | Delete | Delete | Delete
5.3003.3g | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Evaluating Air Flow | Return wet bulb and dry bulb | Return wet bulb and dry bulb air temperatures will be recorded | Ensure equipment operates as designed Ensure equipment operates efficiently Ensure equipment provides comfort Ensure equipment operates safely Ensure equipment is durable | Not Yet Reviewed | 2017-01-16 | 2017-01-16 | State of Alaska... | Beyond most technicians ability | Test not generally needed | Yes more equipment and training | Accepted with Modifications | Combining 5.3003.3f with 5.3003.3g (eliminate Specification row g). Rewritten for clarity |  | Delete | Delete | Delete
5.3003.6a | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Evaluating Sequence of Operation | Verification | The sequence of operation of the system will be verified in accordance with the manufacturer installation, operation, and maintenance manual | Ensure system components function and operate in the correct sequence | Not Yet Reviewed | 2017-01-20 | 2017-01-20 | Bruce Hagen | Often no information available. | Add - When no manual is available the technician will have to rely on standard expected testing results. | No | Accepted with Modifications | Operation manual is not always available |  | No change | The sequence of operation of the system will be verified in accordance with the manufacturer installation, operation, and maintenance manual. If every effort to secure the manufacturer's manual proves unsuccessful, the technician will rely on standard industry testing protocols. | No change
5.3101.1a | Single-Family Homes | Heating and Cooling | Hydronic Heating (Hot Water and Steam) | Design | Heat Load Calculation&mdash;Whole House | Heating load calculation | Load calculation will be performed in accordance with ANSI ANSI American National Standards Institute, www.ansi.org / ACCA ACCA Air Conditioning Contractors of America, www.acca.org 2 Manual J-2011 (Residential Load Calculation) and manufacturer specifications | Enable proper sizing of the heating appliance | Not Yet Reviewed | 2017-01-20 | 2017-01-20 | Kelly Cutchin C... | Most energy modeling software used in efficiency programs include sizing calculations. | Load calculation will be performed in accordance with ANSI/ACCA 2 Manual J-2011 (Residential Load Calculation) or an approved energy modeling program, and manufacturer specifications. | No | Accepted with Modifications | Most energy modeling software used in utility or other incentive-based energy efficiency programs include sizing calculations |  | No change | Load calculation will be performed in accordance with ANSI ANSI American National Standards Institute / ACCA ACCA Air Conditioning Contractors of AmericaManual J (Residential Load Calculation) or equivalent, and manufacturer specifications | No change
5.3101.1b | Single-Family Homes | Heating and Cooling | Hydronic Heating (Hot Water and Steam) | Design | Heat Load Calculation&mdash;Whole House | Equipment selection | Equipment selection will be performed in accordance with ANSI ANSI American National Standards Institute, www.ansi.org / ACCA ACCA Air Conditioning Contractors of America, www.acca.org Manual S and manufacturer specifications | Ensure equipment is able to heat the house | Not Yet Reviewed | 2017-01-20 | 2017-01-20 | Kelly Cutchin C... | Energy modeling software that includes these factors make the Manual S redundant. | Equipment selection will be performed in accordance with ANSI/ACCA Manual 2 or an approved energy modeling program, and manufacturer specifications. | No | Accepted with Modifications | Modeling software may do sizing, but not selection. Maintenance Committee has changed language to reflect that there are other sizing methods available that are equivalent to ANSI/ACCA Manual S |  | No change | Equipment selection will be performed in accordance with ANSI ANSI American National Standards Institute, www.ansi.org / ACCA ACCA Air Conditioning Contractors of America, www.acca.org Manual S or equivalent, and manufacturer specifications | No change
5.3101.2a | Single-Family Homes | Heating and Cooling | Hydronic Heating (Hot Water and Steam) | Design | Space Load Calculation&mdash;Heat Emitter Sizing | Space load calculation | Load calculation will be performed in accordance with ANSI ANSI American National Standards Institute, www.ansi.org / ACCA ACCA Air Conditioning Contractors of America, www.acca.org 2 Manual J-2011 (Residential Load Calculation) and manufacturer specifications | Enable proper sizing of the heating appliance | Not Yet Reviewed | 2017-01-20 | 2017-01-20 | Kelly Cutchin C... | If an auditor is using an energy modeling software approved by the program he or she is working in, that software's sizing calculations must be adequate. | Load calculation will be performed in accordance with ANSI/ACCA 2 Manual J-2011 (Residential Load Calculation) or an approved energy modeling program, and manufacturer specifications. | No | Accepted with Modifications | Braodening the tools used for sizing of heat emitter |  | No change | Load calculation will be performed in accordance with ANSI ANSI American National Standards Institute, www.ansi.org / ACCA ACCA Air Conditioning Contractors of America, www.acca.org 2 Manual J (Residential Load Calculation) or equivalent, and manufacturer specifications | No change
5.3104.9s | Multifamily Homes | Heating and Cooling | Hydronic Heating (Hot Water and Steam) | Equipment Maintenance, Testing, and Repair | Inspection Checklist | Occupant health and safety | All homes with combustion appliances will have a carbon monoxide ( CO CO Carbon monoxide ) detector/alarm If determined to be older than 5 years old, CO CO Carbon monoxide detector/alarm will be replacedAmbient CO CO Carbon monoxide will be maintained at or under 5 ppm or no higher than ambient outside air levels, whichever is higher | Ensure occupant health and safety | Not Yet Reviewed | 2015-12-15 | 2015-12-15 | Kelly Cutchin C... | Other ambient CO levels are referenced (typically 35 ppm) throughout these SWS. As far as I'm aware, no commercially available CO alarms register levels below 9 ppm, and most not below 35 ppm. | Remove last sentence referencing ambient CO at or below 5 ppm. | No. | Accepted with Modifications | Aligned with 2.0203.8, Combustion safety occupant education |  | No change | All homes will have a functioning CO alarm If determined to be more than 5 years old, CO detector/alarm will be replaced If CO levels in interior living spaces exceed outdoor levels, potential sources will be investigated and appropriate action taken to reduce them (e.g., have a qualified professional tune, repair, or replace improperly operating combustion appliances; apply weather stripping or conduct air sealing between the garage or crawl space and the home) | No change
6.6002.1e | Single-Family Homes | Ventilation | Exhaust | Components | Ducts | Duct materials | Flexible materials will be UL UL Underwriters Laboratories 181 listed or Air Diffusion Council approvedRigid, kitchen fans gauges shall meet code requirements or authority having jurisdiction | Effectively move the required volume of airPreserve the integrity of the duct system | Not Yet Reviewed | 2016-03-16 | 2016-03-16 | Adrian Correa | the phrase "kitchen fans" as written is a plural noun, not a possessive noun. Gauges is also a plural noun, not a possessive noun. The word gauges seems out of place entirely. I can find no reference anywhere to a type of gauge which might be considered a "kitchen fan gauge(s)", "kitchen's fan gauge(s)", nor "kitchen fans gauge(s)". Also, the phrase "authority having jurisdiction" is a personal pronoun but is being used as a modifier for the word "requirements". The phrase, "Shall meet ... authority having jurisdiction" is lacking an object. The intended object I believe is the word "requirements". In other words, the phrase, "Shall meet ... authority having jurisdiction" means to have a meeting with, not to comply with. How can you comply with an organization? You comply with a regular noun such as, "instructions, regulations, specifications, orders, wishes, commands, etc." not with an organization. | Delete the entire phrase "Rigid, kitchen fans gauges shall meet code requirements or authority having jurisdiction" or correct to show intended specification. Or, if corrected, rearrange to read, "... shall meet code or authority having jurisdiction requirements". | No, it should decrease the cost as no new items, such as gauges for kitchen fans need be invented, manufactured, distributed, purchased, trained on the use of, nor carried to a job site for use. | Accepted | Reworded last sentence "Rigid, kitchen fans gauges shall meet code requirements or authority having jurisdiction", because it had originally been written incorrectly. |  | No change | Flexible materials will be UL 181 listed or Air Diffusion Council approved The metal gauge of rigid kitchen fan ducting shall meet code requirements or the approval of the authority having jurisdiction. | No change
6.6002.2f | Single-Family Homes | Ventilation | Exhaust | Components | Terminations | Termination location | Terminations will be ducted to the outdoors, which does not include unconditioned spaces such as attics and crawl spaces that are ventilated with the outdoors.Terminations will be installed:A minimum of 3' away from any property lineA minimum of 3' away from operable opening to housesA minimum of 10' away from mechanical intakeAs required by authority having jurisdiction | Prevent exhaust from reentering house | Not Yet Reviewed | 2016-05-03 | 2016-05-03 | Matthew Stewart | Our concern is that warmer moist air will re-enter the attic and this is true with soffits where the vent termination points down and the warm moist air will rise back into the soffit. For a gable-end with the vent punching through the louvered opening at the top the warm moist air will not travel down and back into the attic. | Termination through a gable-end louver of a bath fan vent is acceptable if it is at the top of the louver. | No. It will reduce cost in many instances. | Rejected | SWS is a minimum guideline. If AHJ does not allow a certain termination location, then it should not be terminated as such. Embeded document shows new Gable End Detail (4.1003.15)
6.6005.1a | Single-Family Homes | Ventilation | Exhaust | Appliance Exhaust Vents | Clothes Dryer | Clothes dryer ducting | Clothes dryers will be ducted to the outdoors, which does not include unconditioned spaces such as attics and crawl spaces that are ventilated with the outdoorsAs short a run as practical of rigid sheet metal or semi-rigid sheet metal venting material will be used in accordance with manufacturer specificationsDryer ducts exceeding 35' in duct equivalent length will have a dryer booster fan installedPlastic venting material will not be usedUninsulated clothes dryer duct will not pass through unconditioned spaces such as attics and crawl spacesDucts will be connected and sealed as follows: UL UL Underwriters Laboratories listed foil type or semi-rigid sheet metal to rigid metal will be fastened with clampOther specialized duct fittings will be fastened in accordance with manufacturer specificationsIn addition to mechanical fasteners, duct connections will be sealed with UL UL Underwriters Laboratories 181B or 181B-M listed materialIn addition:Sheet metal screws or other fasteners that will obstruct the exhaust flow will not be usedCondensing dryers will be plumbed to a drain | Preserve integrity of building envelope Envelope The separation between the interior and exterior environments of a building that includes a combination of air and thermal barrier Effectively move air from clothes dryer to outside | Not Yet Reviewed | 2017-01-20 | 2017-01-20 | Kelly Cutchin C... | Some climates don't require insulated dryer ductwork in order to prevent condensation. | CHANGE THIS LINE AS FOLLOWS: Uninsulated clothes dryer duct will not pass through unconditioned spaces such as attics and crawl spaces, except where uninsulated dryer ducting is allowed by code. | No | Accepted | Some climates don't require insulated dryer ductwork in order to prevent condensation. This will be determined by the authority having jurisdiction. |  | No change | All other specs stay. The one below is edited as follows (this is the 5th paragraph in the eixisting spec): Uninsulated clothes dryer duct will not pass through unconditioned spaces such as attics and crawl spaces, except where allowed by the authority having jurisdiction | No change
6.6005.1c | Single-Family Homes | Ventilation | Exhaust | Appliance Exhaust Vents | Clothes Dryer | Make-up air | Make-up air will be provided in accordance with the current version of ASHRAE ASHRAE American Society of Heating, Refrigerating and Air-Conditioning Engineers, www.ashrae.org 62.2 and in compliance with the authority having jurisdiction | Preserve integrity of building envelope Envelope The separation between the interior and exterior environments of a building that includes a combination of air and thermal barrier Effectively move air from clothes dryer to outside | Not Yet Reviewed | 2017-01-20 | 2017-01-20 | Kelly Cutchin C... | Performance based testing will identify the need for make-up air. If it is done, we should be allowed to act on the results. | When worst-case CAZ testing or other performance based testing is done and identifies a need for additional make-up air, make-up air will be provided in accordance with the current version of ASHRAE 62.2 and in compliance with the authority having jurisdiction. If no performance based testing is conducted, make-up air will be provided prescriptively in accordance with the current version of ASHRAE 62.2 and in compliance with the authority having jurisdiction | No | Accepted with Modifications | In homes with atmospherically vented combustion appliances, performance based testing will identify the need for make-up air. If the test identifies the need for make-up air, the user should act on the results. |  | No change | If natural draft combustion appliances are present and if worst-case CAZ and/or other performance based testing is conducted and indicates a need for make-up air, make-up air will be provided in accordance with the current version of ASHRAE 62.2 and in compliance with the authority having jurisdiction. If natural draft combustion appliances are present and if no performance based testing is conducted, make-up air will be provided prescriptively in accordance with the current version of ASHRAE 62.2 and in compliance with the authority having jurisdiction. | No change
6.6005.2e | Single-Family Homes | Ventilation | Exhaust | Appliance Exhaust Vents | Kitchen Range | Make-up air | Make-up air will be provided in accordance with the current version of ASHRAE ASHRAE American Society of Heating, Refrigerating and Air-Conditioning Engineers, www.ashrae.org 62.2 and in compliance with the authority having jurisdiction | Ensure safe operation of combustion appliancesEnsure occupant health and safety | Not Yet Reviewed | 2017-01-20 | 2017-01-20 | Kelly Cutchin C... | We should be able to act based on the results of performance based testing, else why are those tests required? | When worst-case CAZ and/or other performance based testing is conducted and indicates a need for make-up air, make-up air will be provided in accordance with the current version of ASHRAE 62.2 and in compliance with the authority having jurisdiction. When no performance based testing is conducted, make-up air will be provided prescriptively in accordance with the current version of ASHRAE 62.2 and in compliance with the authority having jurisdiction | No | Accepted with Modifications | In homes with atmospherically vented combustion appliances, performance based testing will identify the need for make-up air. If the test identifies the need for make-up air, the user should act on the results. |  | No change | If natural draft combustion appliances are present and if worst-case CAZ and/or other performance based testing is conducted and indicates a need for make-up air, make-up air will be provided in accordance with the current version of ASHRAE 62.2 and in compliance with the authority having jurisdiction. If natural draft combustion appliances are present and if no performance based testing is conducted, make-up air will be provided prescriptively in accordance with the current version of ASHRAE 62.2 and in compliance with the authority having jurisdiction. | No change
6.6201.2a | Single-Family Homes | Ventilation | Whole Building Ventilation | Air Flow Requirements | Primary Ventilation Air Flow between Rooms | Balancing pressure | An appropriate means of pressure balancing will be installed (e.g., transfer grilles, jumper ducts, individual room returns)No room will exceed +/- 3 pascals with reference to the outdoors with all interior doors closed and ventilation systems running | Ensure free flow of air between roomsPreserve integrity of the building envelope Envelope The separation between the interior and exterior environments of a building that includes a combination of air and thermal barrier | Not Yet Reviewed | 2017-01-15 | 2017-01-15 | William Kraus | Changing this would align the single family and the manufactured home specifications for room pressures. | Why are we checking WRT outside for single family this section but in the manufactured home specification 6.6205.1c we check WRT common area. I would think of we want to ensure free flow of air between rooms we should check WRT common area for both these specifications. | No | Accepted | Change "outdoors" to "common area" to align with Manufactured Housing Detail |  | No change | An appropriate means of pressure balancing will be installed (e.g., transfer grilles, jumper ducts, individual room returns) No room will exceed +/- 3 pascals with reference to the common area with all interior doors closed and ventilation systems running | No change
6.6205.1c | Manufactured Housing | Ventilation | Whole Building Ventilation | Exhaust-Only System | Manufactured Housing Exhaust-Only Strategies | Location | No resistance greater than 3 pascals will exist between fan intake location with reference to the common areaExhaust ventilation for common spaces will not be installed in bathrooms or bedrooms | Ensure fresh air distribution to common areas | Not Yet Reviewed | 2017-01-20 | 2017-01-20 | bryan burris | The stipulation that no more that 3 Pa will exist between fan and common area is ok. If the resistance is < 3 Pa, what difference does it make if its located in those areas? Also, we rely heavily on client education for so many aspects of ASHRAE implementation, why would this be any different? "Please keep the door open when the bathroom is not being used." | "No resistance greater than 3 Pa will exist between the fan intake location WRT common area" Omit "Exhaust ventilation for common spaces will not be installed in bathrooms or bedrooms" | No. It will likely reduce costs. | Accepted with Modifications | Spec was rewritten in redline |  | No change | No resistance greater than 3 pascals will exist between fan intake location with reference to the common area | No change
7.8001.1a | Single-Family Homes | Baseload | Plug Load | Refrigerators/Freezers | Refrigerator and Freezer Replacement | Selection | Appliance shall be ENERGY STAR® ratedAppliance will fit in the available space without blocking access to light switches, cabinets, etc.Appliance will carry a minimum one-year warranty that will provide a replacement appliance if repeated issues relating to health, safety, or performance occur | Energy efficient appliance installed | Not Yet Reviewed | 2017-01-20 | 2017-01-20 | Kelly Cutchin C... | If the purpose is to save energy, this allows the most flexibility. | Change first sentence to read: Appliance shall be ENERGY STAR® rated or equivalent energy usage | No | Accepted | This allows users to install appliances that may be as energy efficient, or maree energy efficient, than ENERGY STAR appliances, but are not certified under the ENERGY STAR program |  | No change | Appliance shall be ENERGY STAR® qualified or at least as energy efficient. The other paragraphs will remain unchanged | No change
7.8003.11b | Multifamily Homes | Baseload | Plug Load | Lighting | Lamp Replacement | Selection | Lamps will be compatible with existing fixturesLamps will meet the appropriate nationally recognized product standard ( UL UL Underwriters Laboratories 542, UL UL Underwriters Laboratories 1570)Outdoor lamps will be suitable for local climate conditions and in accordance with ANSI ANSI American National Standards Institute, www.ansi.org / UL UL Underwriters Laboratories product standardsScrew base lamp replacements will be ENERGY STAR® qualified or exceed EISA 2014 standard levels by at least 20% Compact fluorescent lamps and light emitting diode lamps will be ENERGY STAR qualifiedLinear fluorescent lamps will not be replaced with a T12, and T8 lamps will be minimum standard installedLiving space lamps will be a correlated color temperature of less than 3000 kelvinVandal-proof pin-based lamps will be used, if appropriate | Reduce energy useEnsure device functions properlyEnsure product safetyEnsure occupant satisfaction | Not Yet Reviewed | 2017-01-20 | 2017-01-20 | Kelly Cutchin C... | Added "or equivalent" to energy star language, remove 3000 kelvin language - in the Pacific Northwest, the higher CCT lamps are preferred for their brighter light and anti-depressant qualities. We should allow them to be used. | Lamps will be compatible with existing fixtures Lamps will meet the appropriate nationally recognized product standard (UL 542, UL 1570) Outdoor lamps will be suitable for local climate conditions and in accordance with ANSI/UL product standards Screw base lamp replacements will be ENERGY STAR® qualified or exceed EISA 2014 standard levels by at least 20% Compact fluorescent lamps and light emitting diode lamps will be ENERGY STAR qualified or equivalent energy usage Linear fluorescent lamps will not be replaced with a T12, and T8 lamps will be minimum standard installed Living space lamps will be selected in a correlated color temperature deemed acceptable for the region Vandal-proof pin-based lamps will be used, if appropriate | No | Accepted | This allows users to install appliances that may be as energy efficient, or maree energy efficient, than ENERGY STAR appliances, but are not certified under the ENERGY STAR program Removed reference to maximum color temperature of 3000K. In some regions, higher color temperature lighting is prefered. |  | No change | Lamps will be compatible with existing fixtures Lamps will meet the appropriate nationally recognized product standard (UL 542, UL 1570) Outdoor lamps will be suitable for local climate conditions and in accordance with ANSI / ULproduct standards Screw base lamp replacements will be ENERGY STAR® qualified or at least as energy efficient Compact fluorescent lamps and light emitting diode lamps will be ENERGY STAR qualified or at lease as energy efficient Linear fluorescent lamps will not be replaced with a T12, and T8 lamps will be minimum standard installed Vandal-proof pin-based lamps will be used, if appropriate | No change
7.8003.14b | Multifamily Homes | Baseload | Plug Load | Lighting | Fixture Replacement | Selection | Hard-wired indoor fixtures will be in accordance with ANSI ANSI American National Standards Institute, www.ansi.org / UL UL Underwriters Laboratories 1598Plug-in indoor fixtures will be in accordance with ANSI ANSI American National Standards Institute, www.ansi.org / UL UL Underwriters Laboratories 153Hard-wired outdoor fixtures will be suitable for local climatic conditions and in accordance with ANSI ANSI American National Standards Institute, www.ansi.org / UL UL Underwriters Laboratories product standardsFixture will be capable of being attached to existing wiring Fixture will carry at least a 1-year warrantyExisting emergency fixtures will be replaced with new emergency fixturesIn-unit replacement fixtures will be ENERGY STAR® qualifiedFixture will comply with selection criteria of SWS 7.8003.11 Lamp Replacement and SWS 7.8003.13 Ballast Replacement | Reduce energy useEnsure device functions appropriatelyEnsure product safetyEnsure occupant safety | Not Yet Reviewed | 2017-01-20 | 2017-01-20 | Kelly Cutchin C... | Some emergency fixtures might be state of the art but SWS implies replacing them all. Some fixtures are not yet ENERGY STAR qualified but use the same or less energy. | Change these two lines as follows, leave all else as is: Existing emergency fixtures will be replaced with new emergency fixtures when doing so will cost-effectively save energy In-unit replacement fixtures will be ENERGY STAR® qualified or of equivalent energy usage | No | Accepted with Modifications | Since the original SWS were written, there are now many energy star options available. It is not necessary to replace emergency fixtures if they are functioning properly |  | No change | Test existing emergency fixtures and repair or replace if necessary This is the only paragraph that is changed. All others remain unchanged. This is the 6th paragraph | No change
7.8003.1b | Single-Family Homes | Baseload | Plug Load | Lighting | Lighting Upgrade | Selection | All bulbs, fixtures, and controls will be appropriate for the intended application (e.g., enclosed, orientation, dimmable, potential for breakage, indoor, and outdoor)All bulbs, fixtures, and controls will be selected to provide the brightness and light quality required in that application (e.g., task lighting, trip-and- fall hazards, nightlights)Selected equipment should have the highest level of efficiency within a technology [e.g., compact fluorescent lamp ( CFL CFL Compact fluorescent lamp ), LED LED Light-emitting diode ]All bulbs, fixtures, and controls will be ENERGY STAR® rated where applicableWhen possible, bulbs, fixtures, and controls will be selected that will facilitate the use of future lighting technologies (e.g., LEDs)When incandescent bulbs cannot be replaced or when occupant chooses not to replace, a dimmer will be selectedLight/lamp wattage should not exceed rated wattage of fixtureBulb replacements will be chosen based on expected durability, light quality, and lifetime energy use of the bulbControls to turn off lights when not needed (e.g., no one in room) will be providedAll bulbs, fixtures, and controls will be UL UL Underwriters Laboratories -approved and installed in accordance with local code(s) and NFPA NFPA National Fire Protection Association, www.nfpa.org 70 National Electric CodeFluorescent light ballasts containing polychlorinated biphenyls (PCBs) will be replaced in accordance with the EPA EPA U.S. Environmental Protection Agency, www.epa.gov 's Healthy Indoor Environment Protocols for Home Energy Upgrades | Provide improved lighting quality at lower energy useSelect equipment that will not be an unnecessary barrier to future technologiesAvoid inferior products and unsatisfied occupants | Not Yet Reviewed | 2016-07-21 | 2016-07-21 | Charles Kurnik | This text (Power quality will be evaluated before new lighting is selected) is in the Manufactured Housing version of this Detail, but not in the Single-Family Version. Is it appropriate to add to single family if it is being done in manufactured housing? | Add the following to Specification: Power quality will be evaluated before new lighting is selected |  | Accepted with Modifications | Power quality is expensive to test, and may not discover problems if they are intermittent. Modern lighting is resilient to poor power quality |  | No change | Remove "Power quality will be evaluated before new lighting is selected" from Manufactured housing | No change
7.8004.2b | Single-Family Homes | Baseload | Plug Load | Laundry | Clothes Dryer Replacement | Installation | Appliance will be installed in accordance with manufacturer specifications (e.g., leveling, plumbing connection, electrical connection, interior lighting) and meet all applicable codesIf existing venting does not meet the following criteria (as well as manufacturer specifications and applicable codes), new venting will be installed using the following specifications:Appliance will be vented to the outside using metal-to-metal or UL UL Underwriters Laboratories listed foil-type venting materialVenting design will meet standards for optimal ventingVenting will not be constricted or blocked and should be free of lint and/or debrisMust be mechanically fastened to connect metal-to-metal and must not catch lint inside venting materialOnly clamps will be used on semi-rigid metal and UL UL Underwriters Laboratories listed foil-type venting materialsPest screen will be installed at the terminationAt least 3' of the vent closest to the exterior of the house will be insulated with a minimum of R-6All dryers, other than condensing dryers, will be vented to the outdoorsIf a combustion appliance is used, combustion safety testing will be performed in accordance with the Health and Safety Chapter of the Standard Work Specifications for Single Family Housing or other equivalent practiceAny penetrations to the exterior of the home created by the installation of the appliance will be sealedEnergy-related appliance controls will be demonstrated to the occupantSpecific information of the proper maintenance of the equipment will be provided to the occupantWarranty information, operation manuals, and installer contact information will be provided to the occupant | Ensure equipment functions as designed Install appliance safely and effectively Ensure house as a whole system is not adversely affecting the proper functioning/venting of equipmentReduce energy useIn case of fuel switching, reduce cost | Not Yet Reviewed | 2017-01-18 | 2017-01-18 | Kelly Cutchin C... | Pest screening on the end of dryer ducts will cause lint to accumulate. | Remove bullet requiring pest screen at termination. This goes against codes in many states. Instead, include language about backdraft damper from dryer vent ducting SWS: https://sws.nrel.gov/spec/660051 | No. | Accepted with Modifications | Requiring pest screen violates code in many jurisdictions. |  | No change | Remove paragraph with pest screen. All other paragraphs to remain unchanged | No change
7.8102.2d | Single-Family Homes | Baseload | Water Heating | Installation and Replacement | Storage-Type Appliance | Emergency drain pan | An emergency drain pan will be installed with sides that extend a minimum of 4" above floor if leakage would cause damage to the home and in accordance with P2801.5 of the 2012 IRC IRC International Residential Code A ¾" drainline or larger will be connected to tapping on pan and terminated in accordance with P2801.5.2 of the 2012 IRC IRC International Residential Code | Collect and safely dispose of water escaping from the storage tank | Not Yet Reviewed | 2017-01-20 | 2017-01-20 | Kelly Cutchin C... | IRC referenced in SWS mentions 1.5", not 4" pan. | An emergency drain pan will be installed with sides that extend a minimum of 1 1/2" above floor if leakage would cause damage to the home and in accordance with P2801.5 of the 2012 IRC A ¾" drainline or larger will be connected to tapping on pan and terminated in accordance with P2801.5.2 of the 2012 IRC | No | Accepted with Modifications | Generalized to be in compliance with IRC |  | No change | An emergency drain pan and drain line shall be installed in accordance with the IRC | No change
7.8102.2e | Single-Family Homes | Baseload | Water Heating | Installation and Replacement | Storage-Type Appliance | Expansion tank | A potable water expansion tank will be installed on the cold water sideA direct connection with no valves between the storage tank and expansion tank will be installed in accordance with the 2012 IRC IRC International Residential Code , authority having jurisdiction, and according to manufacturer specifications | Protect the storage tank from expansion | Not Yet Reviewed | 2017-01-20 | 2017-01-20 | Kelly Cutchin C... | It is my understanding that in areas where code does not require back flow prevention devices, if they are not part of the system, the expansion tanks are ineffective. | Where back flow protection devices exist or are being installed, potable water expansion tank will be installed on the cold water side A direct connection with no valves between the storage tank and expansion tank will be installed in accordance with the 2012 IRC, authority having jurisdiction, and according to manufacturer specifications | No. | Accepted with Modifications | Revised language to generalize to AHJ |  | No change | Expansion tanks will be installed where required and in accordance with the AHJ. | No change
7.8102.2i | Single-Family Homes | Baseload | Water Heating | Installation and Replacement | Storage-Type Appliance | Thermal efficiency | If additional tank insulation is installed, it will be rated a minimum of R-11 and will be installed to manufacturer specificationsIf additional insulation is installed, it will be installed based on fuel type, making sure not to obstruct draft diverter, pressure relief valve, thermostats, hi-limit switch Hi-limit switch A protective electronic switch that keeps a burner from continuing to operate and damage the appliance , plumbing pipes or elements, and thermostat access platesThe first 6' of inlet and outlet piping will be insulated in accordance with manufacturer specificationsPipe insulation must remain 3'' from gas water heater ventHeat traps will be installed on the inlet and outlet piping where not provided by manufacturer | Reduce standby loss Standby loss Heat loss through the outer part of a water heater. Energy that is used even when a device is turned off from near tank piping and storage tankEnsure insulation does not make contact with flue gas venting | Not Yet Reviewed | 2015-11-24 | 2015-11-24 | Kelly Cutchin C... | Some storage type water heaters are direct vent with pac vents. These are low temperature, and don't require the 3" clearance like single and double-wall metal vent pipes do. Allowing insulation of water pipes near the vent when safe will allow for greater thermal efficiency. | Revise this line to read: Where fire safety codes require, pipe insulation must remain 3'' from gas water heater vent | No. | Accepted with Modifications | Addressed in current redline edit, as of 3/19/2017 |  | No change | If additional tank insulation is installed, it will be rated a minimum of R-11 and will be installed to manufacturer specifications If additional insulation is installed, it will be installed based on fuel type, making sure not to obstruct draft diverter, pressure relief valve, thermostats, hi-limit switch, plumbing pipes or elements, and thermostat access plates The first 6' of inlet and outlet piping will be insulated in accordance with manufacturer specifications Combustible pipe insulation must maintain a minimum clearance of 6" from gas water heater draft hood and/or single wall metal pipe. Clearance from vent such as "B" vent should be maintained per vent manufacturer's specifications Heat traps will be installed on the inlet and outlet piping where not provided by manufacturer | No change
7.8102.2m | Manufactured Housing | Baseload | Water Heating | Installation and Replacement | Storage-Type Appliance | Occupant safety | Carbon monoxide alarms will be installed in each dwelling in accordance with ASHRAE ASHRAE American Society of Heating, Refrigerating and Air-Conditioning Engineers, www.ashrae.org 62.2 and authority having local jurisdictionOccupant will be provided information regarding the health effects and risk of high CO CO Carbon monoxide concentrations, as well as a list of monitors that can provide more detail regarding CO CO Carbon monoxide levelsAmbient CO CO Carbon monoxide to be maintained at or under 10 ppm or within acceptable limits as comparable to outside concentrations | Ensure occupant life safety; CO CO Carbon monoxide alarms are designed to detect levels at which occupants might become unable to evacuate | Not Yet Reviewed | 2015-12-15 | 2015-12-15 | Kelly Cutchin C... | Reference other occupant education SWS related to CO Aand occupant safety - https://sws.nrel.gov/spec/202032 - This one here is inconsistent with 5.3104.9s, which recommends levels at or below 5 ppm. | Remove mention ambient CO level of at or below 10 PPM. Remove that entire sentence. | no. | Accepted with Modifications | Edited to aligned with Combustion appliance occupant safety in other SWS Details |  | No change | All homes will have a functioning CO alarm If determined to be more than 5 years old, CO detector/alarm will be replaced If CO levels in interior living spaces exceed outdoor levels, potential sources will be investigated and appropriate action taken to reduce them (e.g., have a qualified professional tune, repair, or replace improperly operating combustion appliances; apply weather stripping or conduct air sealing between the garage or crawl space and the home) | No change
7.8102.3d | Single-Family Homes | Baseload | Water Heating | Installation and Replacement | On-Demand Appliance | Emergency drain pan | An emergency drain pan will be installed with sides that extend a minimum of 4" above floor if leakage would cause damage to the home and in accordance with P2801.5 of the 2012 IRC IRC International Residential Code A ¾" drainline or larger will be connected to tapping on pan and terminated in accordance with P2801.5.2 of the 2012 IRC IRC International Residential Code | Collect and safely dispose of water escaping from the storage tank | Not Yet Reviewed | 2017-01-20 | 2017-01-20 | Kelly Cutchin C... | 2012 IRC P2801.5 referenced in SWS calls for 1 1/2" pan, not 4" as currently stated in SWS. | Install an emergency drain pan under each replacement water heater that is installed in an area that would be damaged in the case of a leak. The pan shall not be less than 1 1/2" deep and shall be of sufficient size and shape to receive all dripping or condensate for the tank or water heater. A ¾" drainline or larger will be connected to tapping on pan and terminated in accordance with P2801.5.2 of the 2012 IRC | No | Accepted with Modifications | Generalized to be in compliance with IRC |  | No change | An emergency drain pan and drain line shall be installed in accordance with the IRC | No change
7.8102.4h | Multifamily Homes | Baseload | Water Heating | Installation and Replacement | Storage Tank-Type Water Heater | Backflow prevention | Backflow prevention will be installed in accordance with manufacturer specifications and all applicable codesBackflow devices shall be tested by a certified backflow assembly tester at the time of installation, repair, or relocation, and not less than on an annual schedule or more often where required by local code | Protect water supply from contamination | Not Yet Reviewed | 2017-01-20 | 2017-01-20 | Kelly Cutchin C... | Suggest removing the maintenance schedule language. This does no fit in an SWS about installation/replacement of equipment. This is more about on-going maintenance schedules, and may fit better elsewhere. | Backflow prevention will be installed in accordance with manufacturer specifications and all applicable codes Backflow devices shall be tested by a certified backflow assembly tester at the time of installation, repair, or relocation. | No | Accepted | Removed the maintenance schedule language. This does no fit in an SWS about installation/replacement of equipment, but instead about on-going maintenance. |  | No change | Backflow prevention will be installed in accordance with manufacturer specifications and all applicable codes Backflow devices shall be tested by a certified backflow assembly tester at the time of installation, repair, or relocation. | No change
7.8103.1d | Single-Family Homes | Baseload | Water Heating | Maintenance/Inspection | Storage-Type Appliance | Potable water expansion tank | A potable water expansion tank will be installed on the cold water sideTanks that leak or have excessive corrosion will be replacedA direct connection with no valves from the expansion tank to the storage tank will be installedConnection will be properly supported with strappingAn expansion tank drain will be included in non-bladder tanksTank will be installed to accepted industry standards, in accordance with the 2012 IRC IRC International Residential Code and according to manufacturer specificationsTanks that are completely full of water will be drained and refilled before being replaced or repairedExpansion tanks with bladders will have air charged to the manufacturer pressure requirements while water is not present in the tankBladder tanks with water inside of the air bladder will be replaced in accordance with manufacturer specifications | Absorb water expansion of the system | Not Yet Reviewed | 2016-01-19 | 2016-01-19 | Mimi Burbage | Based on the variance of the added cost of adding expansion tank to all existing hot water tanks | For new installations only. | no | Accepted with Modifications | Delete entire Specification. It is covered in a section on new installations |  | Delete row | Delete row | Delete row

## Previosuly Adjudicated Comments (hidden)
Classification | Housing Type | Section | Topic | Subtopic | Detail | Title | Existing specification | Objective language | Status | Submitted | Updated | Submitted By | Comment | Justification/substantiation | Cost increase | Committee Adjudication | Committee Rationale for Decision | Proposed Title | Proposed specification | Proposed Objective language
2.0100.1b | Single-Family Homes | Health and Safety | Safe Work Practices | Safe Work Practices | Global Worker Safety | Hand protection | Durable and wrist-protecting gloves will be worn that can withstand work activity | Minimize skin contact with contaminantsProtect hands from sharp objects | Adjudicated - Redline only | 2014-08-06 | 2014-08-06 | Ricardo Trevino | energy efficiency upgrades often involve changing light bulbs, which can be very hot. Gloves should provide protection from burns. In multi family dwellings, for example, an installer may have have many units install energy efficient lights, and does not have the luxury of waiting for the existing high heat bulbs to cool before removing. | For objective(s), add: Insulate hand from exposure to heat. | Will require insulated gloves when handling hot light bulbs | Accepted | Clarifies the objective; OSHA 19190.138(a) uses the term "hazards" for cuts, abrasions, chemical or thermal burns and harmful temperatures | No change | No change | Minimize skin contact with contaminants Protect hands from hazards
2.0100.1c | Single-Family Homes | Health and Safety | Safe Work Practices | Safe Work Practices | Global Worker Safety | Respiratory protection | If the risk of airborne contaminants cannot be prevented, proper respiratory protection will be provided and worn (e.g., N-95 or equivalent face mask)When applying low pressure 2-component spray polyurethane foam, air purifying masks with an organic vapor cartridge and P-100 particulate filter will be usedWhen applying high-pressure SPF SPF Spray polyurethane foam insulation, supplied air respirators (SARs) will be usedConsult MSDSs for respiratory protection requirements | Minimize exposure to airborne contaminants (e.g., insulation materials, mold spores, feces, bacteria, chemicals) | Adjudicated - Redline only | 2014-06-29 | 2014-06-29 | Deborah Downing | SPF - Will be used - Rim Joist |  |  | Rejected | No change is suggested; low and high pressure SPF are already addressed in this specification and objective. (Suggest to commenter to resubmit with more clarity for their comment, invite to comment on appropriate detail and specification) | No change | No change | No change
2.0111.4c | Single-Family Homes | Health and Safety | Safe Work Practices | Basements and Crawl Spaces | Negative Pressure Contamination Control | Pressure | A negative pressure will be maintained in the crawl space with reference to the house while work is being performed in the crawl space | Prevent contaminants from entering house | Adjudicated - Redline only | 2014-07-14 | 2014-07-14 | John Krigger | Does the fan remain after you install the GMB? Is the pressure maintained permanently? Where does the make-up air come from? | I don't understand the point of this standard. |  | Rejected | Existing spec is clear about whether fan remains with language "while work is being performed." Make up air can come from anywhere as long as pressure in crawl WRT home is negative. | No change | No change | No change
2.0111.5a | Manufactured Housing | Health and Safety | Safe Work Practices | Basements and Crawl Spaces | Prework Qualifications (Home Installation) | Installation deficiencies | Any installation deficiencies that may affect worker safety or integrity or installed measures will be repaired before starting work | Ensure site is safe and ready for upgrade | Adjudicated - Redline only | 2014-05-08 | 2014-05-08 | Rachel Romero | This entire detail should apply to single-family and multifamily housing SWS too. Reasoning: All housing types should have this investigation and recommendation. Copy detail to both SF and MF. |  |  | Rejected | This SWS addresses inspection/assessment of installation of manufactured homes Spec 2.0111.2 already addresses this concern for SF | No change | No change | No change
2.0111.5a | Manufactured Housing | Health and Safety | Safe Work Practices | Basements and Crawl Spaces | Prework Qualifications (Home Installation) | Installation deficiencies | Any installation deficiencies that may affect worker safety or integrity or installed measures will be repaired before starting work | Ensure site is safe and ready for upgrade | Adjudicated - Redline only | 2014-07-14 | 2014-07-14 | John Krigger | Is the statement above what you mean. | Any foundation support problems will be repaired before beginning weatherization work. |  | Rejected | This SWS addresses site conditions prior to any weatherization measures and not solely foundation support | No change | No change | No change
2.0201.1a | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Assessment |  |  | Adjudicated - Redline only | 2014-04-21 | 2014-04-21 | Ted Williams | Minimum requirements from the National Fuel Gas Code (NFGC) Chapter 9, and their extraction into the International Fuel Gas Code (IFGC) and IRC Chapter G24 should be the primary means of addressing the second paragraph and should be so cited. Contrary to previous rejections of comments concerning references to the NFGC coverage, citations of IRC provisions would present the same issues (i.e., applicability to new construction and retrofits requiring code official intervention). More importantly, Section 9.1.24 of the NFGC (2015), which is approved by the ANSI Committee, would apply Chapter 9 to agent work implementing the SWS. Agents implementing the SWS without regard to minimum code would be in violation with this requirement. The serving utility should reexamine providing service to such occupancies. | n/a |  | Accepted with modification | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): This paragraph has been deleted in deference to spillage testing in new detail 2.0201.4a
2.0201.1e | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test |  |  | Adjudicated - Redline only | 2013-04-01 | 2013-04-01 | Thom Knoll | At 2.0201.1e, Depressurization Test, there appears to be magic with -3 pa which does not seem consistent with other standards of similar extraction. The BPI BA standard lists -3 pa limit only for a natural draft appliance commonly vented with a water heater. A whole table of values exist, including a lower threshold for orphaned water heater. | n/a |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Based on the new BPI 1200, the limit has been deleted
2.0201.1e | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test |  |  | Adjudicated - Redline only | 2014-03-28 | 2014-03-28 | DAVID CURTICE | Is this depressurization number for a declared appliance? More information is needed | n/a |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Based on the new BPI 1200, the limit has been deleted
2.0201.1e | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test |  |  | Adjudicated - Redline only | 2014-04-14 | 2014-04-14 | Brad Turner | This specification seems to potentially conflict with the more detailed specifications listed under Section 2.0299.1 - Combustion Appliance Depressurization Tables. 2.0299.1 lists various manufacturer's certified negative pressure tolerance ratings, most of which are more negative than the -3 Pa. limit listed in 2.0201.1e. Suggest language such as, "...and will not be more negative than manufacturer's certified negative pressure tolerance ratings listed in 2.0299.1 depending on appliance type and/or configuration in combustion appliance zone." NOTE - BPI HEP Certification exams (Quality Control Inspector, Energy Auditor, Crew Leader) do require candidates to perform Worst Case CAZ Depressurization tests but DO NOT establish any limits/recommendations based on the appliance type/configuration. Candidate is only required to place CAZ in proper Worst Case scenario and carry out remaining CAZ tests under those conditions. This is confusing for trainers/candidates when the exams are supposed to be based on the SWS. | n/a |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Based on the new BPI 1200, the limit has been deleted
2.0201.1e | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test |  |  | Adjudicated - Redline only | 2014-04-21 | 2014-04-21 | Thom Knoll | Prior comment redirect should be 2.0299.1a | n/a |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance):
2.0201.1e | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test |  |  | Adjudicated - Redline only | 2014-04-21 | 2014-04-21 | Gene Elwood | The -3 pascals is in conflict with depressurization limits in 2.0299.1. | n/a |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): All limits have been deleted
2.0201.1e | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test |  |  | Adjudicated - Redline only | 2014-04-21 | 2014-04-21 | Thom Knoll | While this specification lists only -3 pa, at 2.0199.1a is a list of equipment types with differing depressurization limits. Where does the -3 value come from? | n/a |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Detail 2.0299 has been deleted; -3 value deleted
2.0201.1e | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test |  |  | Adjudicated - Redline only | 2014-05-14 | 2014-05-14 | Darrel Tenter Tenter | The limit of -3 pa conflicts with 2.0299.1 Combustion Appliance Depressurization Limits Table, which shows many CAZ depressurization limits depending on equipment. Suggested change to this language: Depressurization test will include exhaust fans, interior door closure, or duct leakage, or a combination thereof, and will not be more negative than the limits contained in 2.0299.1 Combustion Appliance Depressurization Limits Table. |  |  | Accepted with modification | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): All limits have been deleted
2.0201.1e | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test |  |  | Adjudicated - Redline only | 2014-10-20 | 2014-10-20 | Steve Divan | By limiting the depressurization of any combustion zone to -3 pa is in conflict with 2.0299.1a-i. The depressurization limit ranges from -2 to -25 in those sections. Section 2.0201.1e should be changed to allow for differences between appliances detailed in 2.0299.1a-i. | "Depressurization test will include exhaust fans, interior door closure, or duct leakage, or a combination thereof, and will not be more negative than the Manufacturer's certified negative pressure tolerance rating limit when accounting for base pressure" |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): All limits have been deleted
2.0201.1e | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test |  |  | Adjudicated - Redline only | 2014-10-31 | 2014-10-31 | Colorado Energy... | I am confused as what to follow. It states -3 pascals max for depressurization test however 2.0299.1A-I lists depressurization limits for specific appliances. These two specifications appear to be contradictory. | I am confused as what to follow. It states -3 pascals max for depressurization test however 2.0299.1A-I lists depressurization limits for specific appliances. These two specifications appear to be contradictory. |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): All limits have been deleted
2.0201.1e | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test |  |  | Adjudicated - Redline only | 2015-03-30 | 2015-03-30 | Charles Kurnik | Need clarification. | What if it is "more negative"? Should an exhaust fan be turned off? |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): BPI 1200 method now specified
2.0201.1f | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Spillage test |  |  | Adjudicated - Redline only | 2014-04-14 | 2014-04-14 | Brad Turner | BPI HEP Certification Field Exams (Quality Control Inspector, Energy Auditor, Crew Leader) require candidates to identify time limits for spillage, perform spillage tests, and determine if the appliance passes the spillage tests BASED ON BPI STANDARDS (BPI 1200), which are different that the spillage time limits in SWS. Recommend aligning SWS + BPI 1200 + and BPI HEP Field Exam requirements and time limits. | n/a |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Aligned with BPI 1200 and NFGC; moved to new specification 2.0201.4a
2.0201.1f | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Spillage test |  |  | Adjudicated - Redline only | 2014-04-23 | 2014-04-23 | Darrel Tenter Tenter | Gasses as used here is misspelled. The plural form of gas is gases. Gasses is the present tense verb. As in "Foam insulation out-gasses". |  |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance):
2.0201.1f | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Spillage test |  |  | Adjudicated - Redline only | 2014-08-08 | 2014-08-08 | Roger Smith | BPI standards | This standard suggests two minutes for spillage, whereas BPI says one minute. Which is correct? | no | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): This item deleted in favor of new specification--2.0201.4a--which has the spillage requirements
2.0201.1g | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Carbon monoxide ( CO CO Carbon monoxide ) test in appliance vent |  |  | Adjudicated - Redline only | 2014-04-14 | 2014-04-14 | Brad Turner | BPI HEP Certification Field Exams (Quality Control Inspector, Energy Auditor, Crew Leader) require candidates to measure combustion appliance CO and interpret results BASED ON BPI STANDARDS (BPI 1200), which in some cases are different that the CO thresholds in SWS. BPI Standard 1200 references "ANSI/BSR Z223.1/NFPA 54, National Fuel Gas Code, Table G.6: CO Thresholds", siting CO threshold limits which are different from those listed here in SWS. Recommend aligning SWS + BPI 1200 + and BPI HEP Field Exam requirements and threshold limits. | n/a |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Aligned with BPI 1200 and NFGC; moved to new specification 2.0201.4b
2.0201.1i | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Combustion safety testing at completion of retrofitting home |  |  | Adjudicated - Redline only | 2015-01-07 | 2015-01-07 | Steve Divan | We recognize the importance of doing a daily test out when a potential hazardous situation exists, but this should only be required when a trained professional identifies a problem. The vast majority of homes do not require testing on this level. To add an additional level of safety, most programs require a CO alarm be installed in every home at the time of the audit and a final test out at the conclusion of the job. Additionally, 2.0201.1i is in conflict with 2.0201.3h which is the manufactured home CAZ testing requirements. 2.0201.3h simply states that a final combustion test must be completed at project completion. This seems to be a more reasonable and appropriate standard for single family homes also. Any standard should consider whether the appliance is sealed combustion, direct vent or even fan assisted, reasonably consider the level of air sealing performed and consider the original tightness of the building. A blanket requirement to test at the end of each work day regardless of conditions and equipment type is costly and unnecessary. | Final combustion testing will be conducted at project completion to ensure compliance with the above specifications | No, The current SWS will cause costs to rise.The costs associated with training contractors, purchasing the required equipment and paying for contractor or agency staff time to perform these tests would be an unnecessary burden on the WAP program. The potential costs of performing daily testing are significant and have not been shown to be necessary. | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Many programs do NOT install a CO alarm at audit; the importance of combustion safety makes testing at the end of each day important for the overnight safety of the residents
2.0201.2a | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Safety | Outside combustion make-up air |  |  | Adjudicated - Redline only | 2014-05-15 | 2014-05-15 | John Krigger | This detail says combustion testing. Is this the place for this standard? Do you mean to require outdoor combustion air duct for every tuned-up appliance? Every replaced appliance? I disagree that this is necessary. It is expensive and has possible unintended consequences. |  |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): The word "Testing" removed from specification, title now indicates make-up air
2.0201.2a | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Safety | Outside combustion make-up air |  |  | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | I think that this is what the standard means. If not, what does it mean? | For condensing furnaces, install dedicated combustion air pipe directly to the appliance. |  | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): This could also be for other appliances. This is make-up air, not direct-vent air
2.0201.2b | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Safety | New appliances |  |  | Adjudicated - Redline only | 2014-05-15 | 2014-05-15 | John Krigger | The second paragraph needs to be more specific. |  |  | Accepted with modification | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Added clarifying sentence
2.0201.2b | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Safety | New appliances |  |  | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | I've got the code open and have no idea what this standard is saying. The IRC reference is about clearance. What is this standard requiring? | Too vague. Delete |  | Accepted with modification | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Reference to specific section deleted
2.0201.2d | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Safety | Gas ovens |  |  | Adjudicated - Redline only | 2014-04-14 | 2014-04-14 | Brad Turner | BPI HEP Certification Field Exams (Quality Control Inspector, Energy Auditor, Crew Leader) require candidates to measure oven CO and interpret results BASED ON BPI STANDARDS (BPI 1200), which are different than the threshold limits in SWS. BPI Standard 1200 references "ANSI/BSR Z223.1/NFPA 54, National Fuel Gas Code, Table G.6: CO Thresholds", siting an oven CO threshold limit of 225 ppm As Measured, which is different from those thresholds listed here in SWS. Recommend aligning SWS + BPI 1200 + and BPI HEP Field Exam requirements and threshold limits. | n/a |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): 225 as-measured now used
2.0201.2d | Single-Family Homes | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Safety | Gas ovens |  |  | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | I'm getting questions about how 200 lines up with 800 in this case when it lines up with 400 in other sections. | 200/400??? |  | Accepted with modification | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): The requirement has been aligned with BPI 1200 and the NFGC at 225 ppm as-measured
2.0201.3c | Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Venting |  |  | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | Mobile homes built since the early to mid seventies have been required to have sealed combustion, meaning that they have no draft regulator. Slope isn't an issue for mobile home furnaces, which vent straight up. | Verify the presence of a sealed-combustion venting system. Verify that the furnace's chimney and combustion-air delivery are properly connected and aren't damaged. |  | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): This section can apply to older manufactured homes
2.0201.3e | Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test |  |  | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | CAZ testing is required for open combustion appliances and isn't required for sealed combustion appliances. | When a mobile home furnace is operating, the mobile home must have no open combustion heating devices because of the strong negative pressure created by the furnace. |  | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): This section is not about only furnaces or sealed combustion
2.0201.3e | Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test |  |  | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | Site-built spec applied to mobile home as duplicated in 5.3003 | Change to open combustion from natural draft. |  | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Language is considered appropriate
2.0201.3e | Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test |  |  | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | Site-built spec applied to mobile home as duplicated in 5.3003 | Change to open combustion from natural draft. |  | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Language is considered appropriate
2.0201.3e | Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Depressurization test |  |  | Adjudicated - Redline only | 2015-03-30 | 2015-03-30 | Charles Kurnik | When dealing with combustion byproducts, it seems like the guidance should be consistent. | Most parallel details in the Manufactured Housing version (2.0201.3) do not match the single family version (2.0201.1). It seems like they should. |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Single-family and manufactured housing details are now aligned
2.0201.3f | Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Spillage test |  |  | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | Again the sealed combustion mobile home appliance shouldn't spill. | No detectable spillage allowed. |  | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): This section is not only about furnaces or sealed combustion
2.0201.3f | Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Spillage test |  |  | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | If you have an operable furnace and an open-combustion appliance in a mobile, that is unsafe and should be mitigated. Substitute open-combustion for natural draft -- natural draft isn't the problem. | A mobile home furnace should have no detectable spillage because it is sealed combustion. If a mobile home has an open combustion furnace, the home should have both supply and return ducts. |  | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): There are many manufactured homes with natural draft appliances, including water heaters; his section is not just about furnaces, nor about sealed combustion
2.0201.3f | Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Spillage test |  |  | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | Spillage at anything but a very small level is unacceptable in a sealed-combustion appliance. Same problems as 5.3003 | 100/200 dilemma. |  | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): This section is not about sealed combustion equipment
2.0201.3g | Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Carbon monoxide ( CO CO Carbon monoxide ) test in appliance vent |  |  | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | Here is another 100 ppm number that makes no sense in light of the new 200 ppm initiative. This is sealed combustion equipment after all. | 200/400 if you decide to stick with that standard. |  | Accepted with modification | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): This section is not only about furnaces, or about sealed combustion; however, the CO limits have been updated
2.0201.3g | Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Carbon monoxide ( CO CO Carbon monoxide ) test in appliance vent |  |  | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | How do you justify having a higher bar for sealed combustion appliances in mobile homes? | 100/200 dilemma. |  | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): This section is not about sealed combustion equipment
2.0201.3g | Manufactured Housing | Health and Safety | Combustion Safety | Combustion Safety Testing-General | Combustion Appliance Zone (CAZ) Testing | Carbon monoxide ( CO CO Carbon monoxide ) test in appliance vent |  |  | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | Why more stringent for sealed combustion furnaces? | 100/200 dilemma |  | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): This section is not only about furnaces or sealed combustion
2.0203.1a | Single-Family Homes | Health and Safety | Combustion Safety | Vented Gas Appliances | Combustion Air for Natural Draft Appliances | Required combustion air |  |  | Adjudicated - Redline only | 2014-12-18 | 2014-12-18 | John Krigger | I think that many agencies interpret this standard as a requirement to install supplemental combustion air, which is usually unnecessary. I have a section in our field guides outlining a procedure to evaluate combustion air with a combustion analyzer. | During worst-case testing, use a combustion analyzer to measure both CO and oxygen (O2).The O2 is an indicator of excess combustion air, and CO may be an indicator of insufficient combustion air. |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Now specifies that combustion air only gets added when necessary to solve spillage issues
2.0203.2a | Single-Family Homes | Health and Safety | Combustion Safety | Vented Gas Appliances | Combustion Flue Gas&mdash;Orphaned Water Heaters | Spillage testing |  |  | Adjudicated - Redline only | 2014-04-21 | 2014-04-21 | Ted Williams | The two minute threshold is in conflict with the Z21.10.1 design certification standard for safety and is ad hoc. The threshold should be increased to 5 minutes generally or shorter time durations based on additional criteria (e.g., hot vent initial conditions). | n/a |  | Accepted with modification | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Two minutes is now only for appliances presumed to be in warm vent condition (furnaces in heating mode, water heaters); five minutes is specified for furnaces not in heating mode
2.0203.2a | Single-Family Homes | Health and Safety | Combustion Safety | Vented Gas Appliances | Combustion Flue Gas&mdash;Orphaned Water Heaters | Spillage testing |  |  | Adjudicated - Redline only | 2014-04-23 | 2014-04-23 | Darrel Tenter Tenter | Comment related to the desired outcome for this detail. Gasses as used here is misspelled. The plural form of gas is gases. Gasses is the present tense verb. As in "Foam insulation out-gasses". |  |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance):
2.0203.3a | Single-Family Homes | Health and Safety | Combustion Safety | Vented Gas Appliances | Draft Regulation&mdash;Category I Appliance | Assessment |  |  | Adjudicated - Redline only | 2014-04-23 | 2014-04-23 | Darrel Tenter Tenter | Comment related to the desired outcome for this detail. Gasses as used here is misspelled. The plural form of gas is gases. Gasses is the present tense verb. As in "Foam insulation out-gasses". |  |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance):
2.0203.3c | Single-Family Homes | Health and Safety | Combustion Safety | Vented Gas Appliances | Draft Regulation&mdash;Category I Appliance | Retesting spillage |  |  | Adjudicated - Redline only | 2015-12-15 | 2015-12-15 | Kelly Cutchin C... | Align with BPI 1200 | Where is the first mention of testing spillage in this detail? If this is retesting, the vent will already be warm so the 2 minute limited works. Should there be a row added above that mentions spillage testing with the 2 warm/5 cold vent time limits? |  | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Detail was deleted because draft regulators only apply for oil-fired appliances and don't belong in the gas-fired section
2.0203.4c | Manufactured Housing | Health and Safety | Combustion Safety | Vented Gas Appliances | Combustion Air for Natural Draft Appliances | Spillage testing |  |  | Adjudicated - Redline only | 2015-12-15 | 2015-12-15 | Kelly Cutchin C... | Align with BPI 1200 | Spec: If spillage in a combustion appliance with a warm vent exceeds two minutes during pressure testing, specify measures to mitigate. If spillage in a combustion appliance with a cold vent exceeds five minutes during pressure testing, specify measures to mitigate. Objective: Detect excessive spillage of combustion gases. |  | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Detail combined with Detail 2.0203.1; Spec 2.0203.1c was added to include new testing language
2.0203.5a | Manufactured Housing | Health and Safety | Combustion Safety | Vented Gas Appliances | Combustion Flue Gas&#173;&mdash;Orphaned Water Heaters | Spillage testing |  |  | Adjudicated - Redline only | 2015-12-15 | 2015-12-15 | Kelly Cutchin C... | Align with BPI 1200 | Spec: If spillage in a combustion appliance with a warm vent exceeds two minutes during pressure testing, specify measures to mitigate. If spillage in a combustion appliance with a cold vent exceeds five minutes during pressure testing, specify measures to mitigate. Objective: Detect excessive spillage of combustion gases. |  | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Detail was combined with 2.0203.2; Spec 2.0203.2a was modified to include new language
2.0203.5b | Manufactured Housing | Health and Safety | Combustion Safety | Vented Gas Appliances | Combustion Flue Gas&#173;&mdash;Orphaned Water Heaters | Retesting spillage |  |  | Adjudicated - Redline only | 2015-12-15 | 2015-12-15 | Kelly Cutchin C... | Clarify | Objective: Ensure appliance is not spilling longer than 2 minutes with a warm vent. |  | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Detail was combined with 2.0203.2; Spec 2.0203.2c was modified to include new language
2.0203.6c | Manufactured Housing | Health and Safety | Combustion Safety | Vented Gas Appliances | Draft Regulation&mdash;Category I Appliance | Retesting spillage |  |  | Adjudicated - Redline only | 2015-12-15 | 2015-12-15 | Kelly Cutchin C... | Clarify language. | This is about retesting, but is testing for the first time mentioned in this detail? Consider adding a row above this one. Then clarify objective here: Ensure appliance is not spilling longer than 2 minutes with a warm vent. |  | Rejected | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): Detail was deleted because draft regulators only apply for oil-fired appliances and don't belong in the gas-fired section
2.0299.1a | Single-Family Homes | Health and Safety | Combustion Safety | Additional Resources | Combustion Appliance Depressurization Limits Table | Atmospheric water heater only (Category I, natural draft), open-combustion appliances |  |  | Adjudicated - Redline only | 2014-04-21 | 2014-04-21 | Frank Stanonik | Delete this entire section. There is no recognized test procedure to measure the depressurization resistance of gas and oil-fired appliances so there is no such thing as certified negative pressure tolerance rating. If energy upgrades in an existing home lead to a depressurization issue then the preferred action is not to try to fix the newly created problem but rather to not do the upgrades that created the problem. | n/a |  | Accepted | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance):
2.0401.1b | Single-Family Homes | Health and Safety | Moisture | Air Sealing | Air Sealing Moisture Precautions | Moisture precautions for crawl spaces | Exposed earth will be covered with a continuous, durable, sealed Class 1 vapor retarder Vapor retarder A material that slows the passage of water vapor and contains a perm rating above 1 a minimum of 6 mils in thickness Plastic, foil or any other Class 1 vapor barrier Vapor barrier A material that retards the passage of water vapor and contains a perm rating of less than 1 /retarder will not be used in hot-humid climatesAll accessible penetrations between the crawl space or basement and outside will be sealedHoles between the crawl space or basement and the living space will be sealed | Ensure durability of repairsReduce potential for occupant exposure to mold and other moisture-related hazards | Adjudicated - Redline only | 2014-12-09 | 2014-12-09 | Kelly Cutchin C... | As currently written, the spec indicates you would not install ground cover in hot humid climates, but I don't think that's what the authors intended. I think we still want to cover exposed earth in crawls and basements, but want to avoid trapping moisture against potentially cooler-than-outdoor building components. | Revise 2nd paragraph of spec to: Plastic, foil or any other Class 1 vapor barrier/retarder will not be installed in a way that could trap moisture against building materials in hot-humid climates | No. | Accepted with modification | Clarifies the intent of the SWS and removed uneeded langauge related to basements | No change | Exposed earth will be covered with a continuous, durable, sealed Class 1 vapor retarder a minimum of 6 mils in thickness Any vapor retarder shall not encapsulate wood building materials or spray foam Holes between the crawl space and the living space will be sealed | No change
2.0403.1d | Single-Family Homes | Health and Safety | Moisture | Vapor Barriers | Vented Crawl Spaces&mdash;Ground Moisture Barrier | Overlap seams | When seams exist, they will be overlapped a minimum of 12" using reverse or upslope lapping technique Reverse or upslope lapping technique Upper course laps under a lower course to keep the moisture under the barrier | Keep water under the linerReduce the likelihood of damage at seams | Adjudicated - Redline only | 2015-04-15 | 2015-04-15 | John Krigger | If the goal is to exclude water, water vapor, and air from the ground, the seams should be sealed. | When seams exist, they will be overlapped a minimum of 12" using reverse or upslope lapping technique. Seams must be sealed with tape or sealant. |  | Rejected | Current SWS is able to achieve its objective without sealing the seams | No change | No change | No change
2.0403.1e | Single-Family Homes | Health and Safety | Moisture | Vapor Barriers | Vented Crawl Spaces&mdash;Ground Moisture Barrier | Fastening | Ground moisture barrier will be fastened to ground with durable fasteners or ballast(s) and extend a minimum of 6" up the foundation wall | Prevent movement of the ground moisture barrier | Adjudicated - Redline only | 2014-12-05 | 2014-12-05 | John Davies | Fastening up the wall in existing construction is an added cost burden for a weatherization program, generally not necessary and overkill in the dryer areas of the country. | Fastening required when ground moisture barrier is to be installed on sloping ground, high traffic area or when cover will be exposed to wind. | The proposed change allows fastening but does not require it | Accepted | Addresses specifc situation of the SWS. Still meets objective while reducing cost of measure. | No change | When ground moisture barrier is installed on sloping ground, may be exposed to wind, or accessed for routine maintenance or storage it will be fastened to ground with durable fasteners or ballast(s) | No change
2.0403.2e | Single-Family Homes | Health and Safety | Moisture | Vapor Barriers | Closed Crawl Spaces&mdash;Ground Moisture Barriers | Fastening | The air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary and ground moisture barrier will be fastened to the ground to prevent movement in accordance with ASTM ASTM ASTM International, www.astm.org E1643 and manufacturer's recommendations | Prevent movement and uplift of the air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary and ground moisture barrier | Adjudicated - Redline only | 2015-05-29 | 2015-05-29 | Kelly Cutchin C... | Since this detail addresses closed crawl spaces, it is unlikely that wind will cause uplift of the moisture barrier. Suggest rephrasing so only in situations where the space will be disturbed requires the fastening. | In situations where the crawl space is accessed for routine maintenance or storage, the air barrier and ground moisture barrier will be fastened to the ground to prevent movement in accordance with ASTM E1643 and manufacturer's recommendations | No, reduce it. | Accepted with modification | Addresses specifc situation of the SWS. Still meets objective while reducing cost of measure | No change | When ground moisture barrier is installed on sloping ground, or accessed for routine maintenance or storage it will be fastened to ground with durable fasteners or ballast(s) | No change
2.0403.3b | Single-Family Homes | Health and Safety | Moisture | Vapor Barriers | Closed Crawl Spaces&mdash;Vapor Retarders on Walls | Coverage | An air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary and vapor retarder Vapor retarder A material that slows the passage of water vapor and contains a perm rating above 1 will be installed a minimum of 1' or as high as possible above outside grade | Prevent air and moisture penetration | Adjudicated - Redline only | 2014-03-31 | 2014-07-14 | John Krigger | This spec varies from the IRC, which says take the vapor barrier 6 inches up the wall. I think it is bad practice to install a vapor barrier on the inside of a crawl space wall, higher than 6 inches. The vapor barrier reduces drying potential and could harbor pests. What about the ventilation that the IRC requires? I don't think that is always necessary, but the IRC says you need 1/1500 of natural or an exhaust fan connect to the living space or a supply register in the crawl space of a home that doesn't have AC. The "doesn't have AC" is my spec responding to an oversight in the code and in common building practice. | n/a |  | Rejected | Data from www.crawlspaces.org demonstrates that it is not a bad practice; please resubmit your comment if it was misinterpreted by the committee | No change | No change | No change
2.0403.3b | Single-Family Homes | Health and Safety | Moisture | Vapor Barriers | Closed Crawl Spaces&mdash;Vapor Retarders on Walls | Coverage | An air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary and vapor retarder Vapor retarder A material that slows the passage of water vapor and contains a perm rating above 1 will be installed a minimum of 1' or as high as possible above outside grade | Prevent air and moisture penetration | Adjudicated - Redline only | 2014-04-17 | 2014-07-14 | John Krigger | I really don't like the idea of installing vapor barriers on the interior of foundation walls. It is wishful thinking that the vapor barrier will mitigate moisture problems if the exterior wall isn't waterproofed or dampproofed. I think that the 6-inch ground moisture barrier overlap onto the wall is good practice but that running the vapor barrier further up the wall is pointless and could be counterproductive. | n/a |  | Rejected | Data from www.crawlspaces.org demonstrates that it is not a bad practice; please resubmit your comment if it was misinterpreted by the committee | No change | No change | No change
2.0601.1b | Single-Family Homes | Health and Safety | Electrical | Knob and Tube Wiring | Knob and Tube Wiring | Live wire testing | Non-contact testing method will be used to determine if wiring is live | Protect occupant safetyPreserve the integrity and safety of the house | Adjudicated - Redline only | 2014-05-02 | 2014-05-02 | Rachel Romero | Per executive committee, change to "Appropriate testing method will be used to determine if wiring is live by the authority having jurisdiction" Rationale: Non-contact testing was a vague term. |  |  | Rejected | The SWS intends that testing should be conducted without contacting the wire and therefore the language is sufficient | No change | No change | No change
2.0601.1c | Single-Family Homes | Health and Safety | Electrical | Knob and Tube Wiring | Knob and Tube Wiring | Isolation and protection | Live knob and tube will not be covered or surrounded; required by the National Electrical Code ( NEC NEC National Electrical Code ) or authority having jurisdiction A licensed electrical contractor will inspect and certify wiring to be safe and place a warning at all entries to the attic about the presence of knob and tube wiringA dam that does not cover the top will be created to separate insulation from the wire path | Ensure occupant safety Preserve the integrity and safety of the house | Adjudicated - Redline only | 2014-05-02 | 2014-05-02 | Rachel Romero | Per Executive Committee, replace with "Proper clearance will be maintained around live knob and tube; required by the National Electrical Code ( NEC ) or authority having jurisdiction A dam that does not cover the top will be created to separate insulation from the wire path" | Rationale: Defer to the authority having jurisdiction for the inspection requirements. |  | Accepted with modification | Agree with rationale of commenter | No change | Proper clearance will be maintained around live knob and tube as required by the National Electrical Code ( NEC ) or authority having jurisdiction When required, a dam that does not cover the top will be created to separate insulation from the wire path | No change
2.0702.1b | Single-Family Homes | Health and Safety | Occupant Education and Access | Installed Equipment | Warranty and Service Agreement | Warranty renewal and service agreement | An option for annual inspection and renewal of warranty and service agreement for up to 10 years will be offered at a cost (requirement for installers) | Provide occupants with an option for extending the warranty and service agreement | Adjudicated - Redline only | 2014-12-02 | 2014-12-02 | Shawn Turi | I am a contractor not the manufacturer nor am I an underwriter for an Insurance Company. I do not understand how I would be responsible for offering a 10 year replacement warranty for equipment that I only installed but did not build. If the manufacturer does not offer extended parts and labor for their appliances, how then can you make a small, independent businessman be responsible for what the manfacturer should be offering? I will be consulting my lawyer about these concerns. | I feel that the warranty on installed appliances should be for only what the manufactured warranties are. For instance, water heaters have 6 year tank and parts, and furnaces have 10 year parts and limited life time heat exchangers if registerd online within 90 days by the costumer. Ashrae fans usually have a 1 year to 2 year warranty.I propose that the customer be made aware of the manufacturer warranties and not a 10 year replacement and labor warranty. I do agree that I should offer a one year warranty on any materials used and craftmanship of the labor. |  | Accepted | We cannot force installers to offer longer warranties than manufacturers. Suggest following modifications to distiguish between company warranty and manufacturer warranty. | Warranty and Maintenance Agreement - Client Education | Provide occupants with manufacturers' warranties on installed equipment and inform of installer maintenance agreement options Share information on company related annual inspections and maintenance agreements as well as manufacturer related warranty details | Ensure occupants are aware of warranty and maintenance agreement options
3.1001.1a | Single-Family Homes | Air Sealing | Attics | Penetrations and Chases | Penetrations and Chases | Pre-inspection | An inspection will be conducted for mold, water leaks, and water damage before sealing a chaseRepairs will be completed before work | Repair moisture-related issues | Adjudicated - Redline only | 2015-04-15 | 2015-04-15 | Charles Kurnik | This is a test of justification | This is a test of new text |  | Rejected | Test of system, not comment on SWS. | No change | No change | No change
3.1001.4a | Manufactured Housing | Air Sealing | Attics | Penetrations and Chases | General Penetrations (Electrical, HVAC, Plumbing, Vent Termination, Recessed Lighting) | Work assessment | Installer prework assessment will be conducted to determine: Structural integrity Roof leaks Insect infestation Accessibility Number, type, size, and location of penetrations | Ensure work space is safe and ready for air sealingVerify scope of work | Adjudicated - Redline only | 2014-06-29 | 2014-06-29 | Deborah Downing | Testing Template Comments |  |  | Rejected | Test of system, not comment on SWS. | No change | No change | No change
3.1003.1a | Single-Family Homes | Air Sealing | Attics | Dropped Ceilings and Soffits | New Ceiling Below Original&mdash;Old Ceiling Intact or Repairable | Pre-inspection | An inspection will be conducted for mold, water leaks, and water damage before sealing a dropped ceiling or soffitRepairs will be completed before work begins | Repair moisture-related issues | Adjudicated - Redline only | 2014-05-18 | 2014-05-18 | Jeffrey Granger | This is an area for you to enter comments. |  |  | Rejected | Test of system, not comment on SWS. | No change | No change | No change
3.1201.1e | Single-Family Homes | Air Sealing | Windows and Doors | Maintenance, Repair, and Sealing | Double-Hung Wood Windows | Sash replacement | Lower sash will have the same bevel on the bottom rail as the sillSash will be water-sealed and primed | Ensure sash remains in a fixed position when open or partially openMaintain operability of the window | Adjudicated - Redline only | 2015-01-05 | 2015-01-05 | Peter Newton | The bevel of the lower sash should match the bevel of the sill in order to provide a complete seal when closed as well as prevent water infiltration beneath sash. | Form a complete seal from the bottom of the lower sash to the sill. |  | Accepted | Clarifies SWS and achieves stated objective. | No change | No change | Ensure sash remains in a fixed position when open or partially open Maintain operability of the window Form a complete seal from the bottom of the lower sash to the sill
3.1203.1b | Single-Family Homes | Air Sealing | Windows and Doors | Replacement | Replacement Window in Existing Window Frame | Opening preparation | Interior stops, sashes, parting strips, and pulleys will be removedOpening will be cleaned | Provide a clean opening for replacement window unit | Adjudicated - Redline only | 2014-05-09 | 2014-05-09 | Pete Hans | wash windows with cool-aid and paint glass |  |  | Rejected | No justification/substantiation provided. | No change | No change | No change
3.1402.2a | Single-Family Homes | Air Sealing | Basements and Crawl Spaces | Crawl Spaces | Closed Crawl Spaces&mdash;Air Sealing Foundation Vents | Vent closure | Vent opening will be permanently closed and sealed | Prevent air and moisture penetration | Adjudicated - Redline only | 2014-05-14 | 2014-05-14 | Darrel Tenter Tenter | In certain circumstances we should not be permanently sealing off the CS vents. How does this specification not conflict with other specs that define when the CS vents should be sealed, and what must be done first. 2.0404.2 for example. Either delete this specification, or add some a decision points to decide if the CS vents should be sealed or not. |  |  | Rejected | The SWS is not a prescriptive tool for every situation | No change | No change | No change
3.1501.1a | Single-Family Homes | Air Sealing | Attached Garages | Garage Openings | Penetrations, Cracks, and Doors Between Garage and House | Penetrations | All lighting fixtures, wiring, plumbing, venting, ducting, and gas piping penetrations will be sealed | Prevent air leakage and pollutant entry | Adjudicated - Redline only | 2014-09-22 | 2014-09-22 | Nicole Harrison | Reason for edit | Edit |  | Rejected | Test of system, not comment on SWS. | No change | No change | No change
3.1601.8c | Multifamily Homes | Air Sealing | Ducts | Duct Preparation | Preparation and Mechanical Fastening&mdash;Mid and High Rise | Flex to metal (150) | Joints will be fastened with tie bands using a tie band Tie band A strap, often made of nylon, that mechanically squeezes a flexible duct to a fitting. Must have a minimum performance temperature rating of 165° (per UL 181A-type test) and a minimum tensile strength rating of 50 pounds tensioning tool or mechanical band, and sealed with approved mastic and UL181B tape | Ensure joints are durable Reduce air leakage | Adjudicated - Redline only | 2014-12-03 | 2014-12-03 | Jim Harmon Harmon | The joint needs to be (1) secure and (2) sealed. The tie band or mechanical band secures the joint, and the mastic OR tape will seal the joint. Therefore both mastic AND tape would be redundant and a waste of resources. See research by Bruce Manclark. | Joints will be fastened with tie bands using a tie band tensioning tool or mechanical band, and sealed with approved mastic OR UL181B tape |  | Accepted | Clarifies expectations of measure | No change | Joints will be fastened with tie bands using a tie band tensioning tool or mechanical band, and sealed with approved mastic OR UL181B tape. Must have a minimum performance temperature rating of 165° (per UL 181A-type test) and a minimum tensile strength rating of 50 pounds tensioning tool or mechanical band, and sealed with approved mastic and UL181B tape | No change
3.1802.1a | Multifamily Homes | Air Sealing | Roofs | Roof/Wall Connections | Roof/Exterior Wall Connection, Including Joints at Roof/Parapet/Wall Connections | Pre-inspection | Conduct pre-inspection in accordance with SWS 2.0100.4 Work Area Inspection and StabilizationExisting water control measures will be identifiedAir sealing locations will be identified between the roof and the exterior wall | Provide a safe and stable work environmentAvoid compromising existing water control systemEnsure a continuous air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary will be appropriately located at the roof/exterior wall junction | Adjudicated - Redline only | 2014-12-08 | 2014-12-08 | Kelly Cutchin C... | Parapet walls sometimes exist in SF homes, and nothing from this detail would preclude its inclusion in the SF SWS (and hence provide reference for field guides, etc.) | No new text - suggest adding this to Single Family Library (entire detail, not just this row). | No. | Accepted | (No language change. Add detail to SF.) | No change | No change | No change
4.1001.1b | Single-Family Homes | Insulation | Attics | General Preparation | Non-Insulation Contact (IC) Recessed Light | Enclosure top | The top-fire rated enclosure material will have an R-value of 0.5 or lessThe top of the enclosure will be left free of insulation | Prevent heat build up | Adjudicated - Redline only | 2014-11-03 | 2014-11-03 | Steve Divan | 5/8" Sheetrock has an R-value of .56. 4.1001.1a indicates that 5/8" Sheetrock is an acceptable material. The R-value should be changed to avoid any conflict between the two sections. | The top-fire rated enclosure material will have an R-value of 0.56 or less. |  | Accepted | Clarifies SWS and achieves stated objective. | No change | The top-fire rated enclosure material will have an R-value of 0.56 or less The top of the enclosure will be left free of insulation | No change
4.1001.3b | Single-Family Homes | Insulation | Attics | General Preparation | Fireplace Chimney and Combustion Flue Vents | Required clearance | A rigid dam having a height greater than the insulation to be installed will be constructed to ensure a 3" clearance between combustion flue vent and dam Chimney vents will have an airspace clearance to combustibles in accordance with 2012 IRC IRC International Residential Code M1801.3.4 | Ensure dam material does not bend, move, or sagPrevent a fire hazard | Adjudicated - Redline only | 2015-01-26 | 2015-01-26 | John Krigger | Why create a larger area of insulation void than necessary. L-vent is 3, B-vent: 2; masonry interior: 2; masonry exterior: 1 and all fuel:2. These are NFPA figures and plenty conservative. Why require 3"? The IRC section referenced says nothing important. | A rigid dam having a height greater than the insulation to be installed will be constructed to ensure a 3" clearance between combustion flue vent and combustible materials, unless the flue vent is listed for a lesser clearance. |  | Accepted | Clarifies SWS and achieves stated objective. | No change | A rigid dam having a height to ensure a 3" clearance area free of insulation or combustibles between combustion flue vent and dam, unless the flue vent is listed for a lesser clearance | No change
4.1001.3b | Single-Family Homes | Insulation | Attics | General Preparation | Fireplace Chimney and Combustion Flue Vents | Required clearance | A rigid dam having a height greater than the insulation to be installed will be constructed to ensure a 3" clearance between combustion flue vent and dam Chimney vents will have an airspace clearance to combustibles in accordance with 2012 IRC IRC International Residential Code M1801.3.4 | Ensure dam material does not bend, move, or sagPrevent a fire hazard | Adjudicated - Redline only | 2015-04-24 | 2015-04-24 | Kelly Cutchin C... | Consider adding this entire detail to the Manufactured Housing library. Currently, I can't find anything about prepping for attic insulation in MH. | N/A - suggesting adding to MH library. | No. | Accepted | Clarifies SWS and achieves stated objective. | No change | A rigid dam having a height to ensure a 3" clearance area free of insulation or combustibles between combustion flue vent and dam, unless the flue vent is listed for a lesser clearance | No change
4.1002.2b | Single-Family Homes, Manufactured Housing | Insulation | Attics | Above Roof Deck Insulation | Above Deck Roof Deck Insulation: Installation | Installation | Insulation will be installed according to manufacturer specifications without gaps, voids, compressions, misalignments, or wind intrusionsInsulation will be installed to prescribed R-value | Install insulation properly | Adjudicated - Redline only | 2014-06-10 | 2014-06-10 | Rachel Romero | The language here refers to blow-in insulation. Only regisit insulation goes above the roof deck. |  |  | Rejected | Rigid insulation can be installed to allow gaps, voids, and wind intrusion. This SWS clarifies this is not acceptable. | No change | No change | No change
4.1003.1a | Single-Family Homes | Insulation | Attics | Attic Ceilings | Pitched/Vaulted/Cathedralized Ceilings&mdash;Loose Fill Over | Ventilation | Venting will be continuous, if applicable | Ensure capacity to increase R-value while not altering ventilation | Adjudicated - Redline only | 2015-04-15 | 2015-04-15 | John Krigger | I don't understand the text of the specification. "If applicable" sounds like the authors were intentionally vague. | The IRC requires venting the roof cavity or installing foam insulation on the rooftop in addition to filling the cavity. Weatherization allows unvented roof cavities without rooftop foam, where local officials permit it. Roof venting is always preferred if possible and continuous soffit and ridge venting is best practice. |  | Rejected | No real expected outcome given in comment or justification | No change | No change | No change
4.1003.1c | Single-Family Homes | Insulation | Attics | Attic Ceilings | Pitched/Vaulted/Cathedralized Ceilings&mdash;Loose Fill Over | Installation | When using cellulose, stabilized product is preferred when available On roof pitches less than 6/12, loose fill cellulose can be used; on roof pitches greater than 6/12, install Insulweb baffles of the same height as the insulation every 6' across slope to prevent the loose fill insulation from sliding downward, or dense pack Dense pack The process of installing loose-fill insulation to reduce air flow and perform to a stated R-value cellulose above Insulweb stapled to the bottom (underside) of the rafters Loose fill fiberglass will only be used on a slope less than or equal to a 6/12 pitch or the slope application approved by the manufacturer, whichever is less (dense packed fiberglass at slopes greater than 6/12 may be used) Roof cavities will be insulated with loose fill according to manufacturer specifications without gaps, voids, compressions, misalignments, or wind intrusions Insulation will be installed to prescribed R-value | Ensure appropriate material and applicationInsulate to prescribed R-value | Adjudicated - Redline only | 2014-04-23 | 2014-04-23 | Darrel Tenter Tenter | Insulweb is a registered trademark and should bear the ® symbol when used. |  |  | Accepted | Clarifies SWS and achieves stated objective. | No change | When using cellulose, stabilized product is preferred when available On roof pitches less than 6/12, loose fill cellulose can be used; on roof pitches greater than 6/12, install non-woven polypropylene netting (webbing) baffles of the same height as the insulation every 6' across slope to prevent the loose fill insulation from sliding downward, or dense pack cellulose above webbing stapled to the bottom (underside) of the rafters Loose fill fiberglass will only be used on a slope less than or equal to a 6/12 pitch or the slope application approved by the manufacturer, whichever is less (dense packed fiberglass at slopes greater than 6/12 may be used) Roof cavities will be insulated with loose fill according to manufacturer specifications without gaps, voids, compressions, misalignments, or wind intrusions Insulation will be installed to prescribed R-value | No change
4.1003.2a | Single-Family Homes | Insulation | Attics | Attic Ceilings | Pitched/Vaulted/Cathedralized Ceilings&mdash;Dense Pack Over | Fill slant ceilings | Using fill tube, 100% of each cavity will be filled to a consistent density: Cellulose material will be installed to a minimum density of 3.5 pounds per cubic foot Loose fiberglass material will be installed and will be specifically approved for air flow resistance per manufacturer's recommendations The number of bags installed will be confirmed and will match the number required on the coverage chart Insulation will be verified to prevent visible air movement using chemical smoke at 50 pascals of pressure difference | Ensure complete and consistent coverage throughout ceiling planeEliminate voids and settlingMinimize framing cavity air flows | Adjudicated - Redline only | 2014-07-09 | 2014-07-09 | Michael Furze | Insulation will be verified to prevent visible air movement at 50 pascals of pressure difference. | The cost of transporting Chemical smoke through the air makes the product cost prohibitive for the Washington (and New MExico) programs. Alternatives need to be found. | This should decrease cost. | Accepted with modification | Specifically noting "chemical" smoke does not address the issues that Washington and New Mexico are facing. Suggestion of using the terminology "smoke/vapor generating infiltration tools" or along the lines of that should address the commenters issue. | No change | Insulation will be verified to prevent visible air movement at 50 pascals of pressure difference using chemical smoke, IR scans, or other approved verification method. | No change
4.1004.2a | Single-Family Homes | Insulation | Attics | Knee Walls | Preparation for Batt Insulation | Knee wall Knee wall Any wall between the conditioned space and the attic prep for batts | All knee walls will have a top and bottom plate or blockers installed using a rigid material Rigid material Drywall, oriented strand board, duct board, cardboard, or any other stiff product that may support the load of insulation while serving as a durable air barrier All joints, cracks, and penetrations will be sealed in finished material, including interior surface to framing connections | Eliminate bending, sagging, or movement that may result in air leakagePrevent air leakage through the top or bottom of the knee wall Knee wall Any wall between the conditioned space and the attic Create an air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary | Adjudicated - Redline only | 2014-12-08 | 2014-12-08 | Kelly Cutchin C... | Language taken from 4.1004.1. Applies to this detail as well. | When knee wall floor and walls are being insulated, the floor joist running under the knee wall will be air sealed. | It shouldn't. People should be doing this already. | Accepted | Clarifies SWS and achieves stated objective. | No change | All knee walls will have a top and bottom plate or blockers installed using a rigid material Rigid material Drywall, oriented strand board, duct board, cardboard, or any other stiff product that may support the load of insulation while serving as a durable air barrier All joints, cracks, and penetrations will be sealed in finished material, including interior surface to framing connections When knee wall floor and walls are being insulated, the floor joist running under the knee wall will be air sealed. | No change
4.1004.5b | Single-Family Homes | Insulation | Attics | Knee Walls | Knee Walls and Gable End Walls&mdash;Preparation for and Installation of Spray Polyurethane Foam (SPF) | Installation | Insulation will be installed to prescribed R-valueUsing SPF SPF Spray polyurethane foam application, SPF SPF Spray polyurethane foam will be applied to desired thickness onto substrate material from top to bottom plate between studs using pass thickness maximum in accordance with manufacturer specificationsIn colder climates ( IECC IECC International Energy Conservation Code Zones 5-8), the SPF SPF Spray polyurethane foam will be installed to a thickness of at least Class II vapor retarder Vapor retarder A material that slows the passage of water vapor and contains a perm rating above 1 or have at least Class II vapor retarder Vapor retarder A material that slows the passage of water vapor and contains a perm rating above 1 coating or covering in direct contact with the interior of the SPF SPF Spray polyurethane foam | Eliminate cracks, gaps, and voids Minimize framing cavity air flows Minimize moisture migration and unwanted condensation in insulation (vapor retarders)Ensure alignment of insulation and air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary | Adjudicated - Redline only | 2014-04-22 | 2014-04-22 | John Krigger | This standard seem to assume that we're creating a cathedralized attic or else why would we insulate the gable-end wall? Is that the intent of this detail? |  |  | Rejected | SWS does not dictate surfaces to insulate. This SWS applies IF you are insulating Knee Walls or Gable End walls with SPF insulation. No updates needed. | No change | No change | No change
4.1005.2c | Single-Family Homes | Insulation | Attics | Attic Floors | Accessible Floors&mdash;Loose Fill Installation | Installation | All insulation will be installed to the depth indicated on the manufacturer coverage chart for desired R-value | Reduce heating and air conditioning costsImprove comfortMinimize noise | Adjudicated - Redline only | 2014-08-08 | 2014-08-08 | Adrian Correa | The standard as stated does not conform to manufacturer instructions for application of their product. See Greenfiber Attic card, PM-6.3-24 Rev F 01/13, on manufacturer's web site. Loose fill insulation may be installed at varying densities. The manufacturer warrants R-value at a certain temperature only if the density indicated is met. Calculations of density may be stated as indicated depth and minimum bags per 1,000 sq. ft., or as indicated depth and maximum coverage area per bag, etc. This standard as currently written ignores the installed density of loose fill cellulose insulation and assumes installed depth is the only factor at work to ensure desired R-value | All insulation will be installed to the minimum unsettled depth and the maximum coverage per bag for desired R-value indicated on the manufacturer's coverage chart. | This change may cause an insignificant cost in implementation until all applicators understand the factors by which their work is judged. | Accepted | Clarifies SWS and achieves stated objective. | No change | All insulation will be installed to the minimum unsettled depth and the maximum coverage per bag to reach a consistent depth for desired R-value indicated on the manufacturer's coverage chart. | No change
4.1005.3c | Single-Family Homes | Insulation | Attics | Attic Floors | Accessible Floors&mdash;Batt Insulation Over Existing Insulation | Insulation | A dated receipt signed by the installer will be provided that includes:Coverage areaThicknessR-value | Document job completion to contract specificationsConfirm amount of insulation installedEnsure ability to match bags required for total area completedComply with 16 CFR 460.17 | Adjudicated - Redline only | 2014-12-04 | 2014-12-04 | Scott Kashuba | I believe an error was made with the last change- should have changed 4.1005.3e not 4.1005.3c | I believe this language should be in 4.1005.3e The original language should be here that was removed Date Detail/Specification Previous Language 07-17-2014 4.1005.3c Specifications:Batts will be installed in accordance with manufacturer specifications without gaps, voids, compressions, misalignments, or wind intrusionsInsulation will be installed to prescribed R-value 07-17-2014 4.1005.3c Objectives:Insulate to prescribed R-value | No | Accepted | Clarifies SWS and achieves stated objective. | Insulation | Batts will be installed in accordance with manufacturer specifications without gaps, voids, compressions, misalignments, or wind intrusions Insulation will be installed to prescribed R-value | Insulate to prescribed R-value
4.1005.3e | Single-Family Homes | Insulation | Attics | Attic Floors | Accessible Floors&mdash;Batt Insulation Over Existing Insulation | Insulation | A dated receipt signed by the installer will be provided that includes:Coverage areaThicknessR-value | Document job completion to contract specificationsConfirm amount of insulation installedEnsure ability to match bags required for total area completedComply with 16 CFR 460.17 | Adjudicated - Redline only | 2014-12-04 | 2014-12-04 | Scott Kashuba | See above | regarding the previous comment I submitted. If the changes are what were intended (probably were) then the title needs changed from "Insulation" to "Onsite documentation" | No | Accepted | Changed title row for 4.1005.3e to "Onsite documentation" | Onsite documentation | A dated receipt signed by the installer will be provided that includes: Coverage area Thickness R-value | Document job completion to contract specifications Confirm amount of insulation installed Ensure ability to match bags required for total area completed Comply with 16 CFR 460.17
4.1005.6a | Single-Family Homes | Insulation | Attics | Attic Floors | Enclosed Attic Storage Platform Floor&mdash;Dense Pack Installation | Fill floors | Each cavity will be 100% filled to consistent density: Cellulose material will be installed to a minimum density of 3.5 pounds per cubic foot. Loose fiberglass material will be installed and will be specifically approved for air flow resistance to a minimum density per the manufacturer's recommendations The number of bags installed will be confirmed and will match the number required on the coverage chart Insulation will be verified to prevent visible air movement using chemical smoke at 50 pascals of pressure difference | Eliminate voids and settling Minimize framing cavity air flows | Adjudicated - Redline only | 2014-04-22 | 2014-04-22 | John Krigger | I like this standard because it specifies density and says to use fiberglass that can achieve that density. I wouldn't count on the typical coverage chart or manufacturers' specifications for guidance like you do in some other details. I might prefer a medium pack for this type of assembly to limit the pressure on the ceiling. Could we have densities for open blow, medium pack, and dense pack? |  |  | Accepted | Clarifies measure to reduce blowing out walls | No change | Each cavity will be 100% filled to consistent density: Cellulose material will be installed to a minimum density of 3.5 pounds per cubic foot or to a maximum density structurally allowable Loose fiberglass material will be installed and will be specifically approved for air flow resistance to a minimum density per the manufacturer's recommendations The number of bags installed will be confirmed and will match the number required on the coverage chart Insulation will be verified to prevent visible air movement using chemical smoke at 50 pascals of pressure difference | No change
4.1005.6c | Single-Family Homes | Insulation | Attics | Attic Floors | Enclosed Attic Storage Platform Floor&mdash;Dense Pack Installation | Onsite documentation | A dated receipt signed by the installer will be provided that includes:Coverage areaThicknessR-value | Document job completion to contract specificationsConfirm amount of insulation installedComply with 16 CFR 460.17 | Adjudicated - Redline only | 2014-04-22 | 2014-04-22 | John Krigger | Could you explain the different documentation requirements in its own section and listing what type of assembly requires what type of documentation. We don't expect the reader to have a copy of 16m CFR 460 do we? I see a variety of stated requirements and don't understand why they are different. |  |  | Rejected | Installer doesn't need copy of 16 CFR 460. Requirements are listed in the spec. Requirements vary slightly by insulation type. | No change | No change | No change
4.1005.7c | Single-Family Homes | Insulation | Attics | Attic Floors | Attic Floor&mdash;Preparation and Installation of Spray Polyurethane Foam (SPF) | Safety | Insulation will not be allowed on top of non- IC IC Insulation contact rated can light Can light A light fixture (or can) that is recessed into the ceiling boxes or between a heat-generating appliance and a dam, unless material is rated for co+H9ntact with heat-generating sources | Prevent a fire hazard | Adjudicated - Redline only | 2014-04-22 | 2014-04-22 | John Krigger | Spray foam should never be installed over light fixtures. First the R-value and direct contact can overheat the fixture causing a fire hazard or cycling the safety switch on an IC rated device. Second the temperature limit of the foam is likely to be exceeded and the foam may outgas and degrade. |  |  | Accepted | Prevent a fire hazard | No change | Spray foam should never be installed over light fixtures regardless of if fixture is rated for IC or not. Nor between a heat-generating appliance and a dam, unless material is rated for contact with heat-generating sources. | No change
4.1006.1a | Single-Family Homes | Insulation | Attics | Attic Openings | Pull-Down Stairs | Installation | Hatches will be insulated to the maximum R-value structurally allowable up to the R-value of the adjoining insulated assemblyPull-down stair rough opening will be surrounded with a durable dam that is higher than the level of the attic floor insulationCounter-weights should be considered to ease accessibility for excessively heavy hatches | Achieve uniform R-valuePrevent loose insulation from entering the living area | Adjudicated - Redline only | 2014-06-13 | 2014-06-13 | CARL Raben | 6.11 |  |  | Rejected | No comment submitted. | No change | No change | No change
4.1006.1d | Single-Family Homes | Insulation | Attics | Attic Openings | Pull-Down Stairs | Occupant education | A dated receipt signed by the installer will be provided that includes:Coverage areaThicknessR-value | Document job completion to contract specificationsConfirm amount of insulation installedComply with 16 CFR 460.17 | Adjudicated - Redline only | 2014-12-04 | 2014-12-04 | Scott Kashuba | See above | to be consistent the title should be "Onsite documentation" | No | Accepted | Clarifies SWS and achieves stated objective. | Onsite documentation | No change | No change
4.1006.2b | Single-Family Homes | Insulation | Attics | Attic Openings | Access Doors and Hatches | Sealing | Access hatch frames will be sealed using caulk, gasket, weather-strip, or otherwise sealed with an air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary material, suitable film, or solid material Options will include installing a latch or lock or frictionally engaged components of a pre-fabricated unit above the opening that do not require a latch The measure must include a protective baffle or insulation barrier | Prevent air leakage | Adjudicated - Redline only | 2014-08-05 | 2014-08-05 | Judith Darst | Follow-up question: Our current spec calls for "tight-fitting" so as long as the hatch is snug and held in by gravity, this complies without a latch. For some hatch configurations, it will be difficult to install a latch and could possibly create an air leakage problem. | Question: What do you mean by "frictionally engaged components?" Is "tight fitting" and frictionally engaged" the same? Does gravity comply with "frictionally engaged?" | No, looking for clarification. | Accepted | Removed pre-fabricated language | No change | Access hatch frames will be sealed using caulk, gasket, weather-strip, or otherwise sealed with an air barrier material, suitable film, or solid material Options will include installing a latch or lock or frictionally engaged components that do not require a latch The measure must include a protective baffle or insulation barrier | No change
4.1006.2e | Single-Family Homes | Insulation | Attics | Attic Openings | Access Doors and Hatches | Occupant education | A dated receipt signed by the installer will be provided that includes:Coverage areaThicknessR-value | Document job completion to contract specificationsConfirm amount of insulation installedComply with 16 CFR 460.17 | Adjudicated - Redline only | 2014-12-04 | 2014-12-04 | Scott Kashuba | see above | Title should be "Onsite documentation" for consistency | no | Accepted | Clarifies SWS and achieves stated objective. | Onsite documentation | No change | No change
4.1006.3a | Single-Family Homes | Insulation | Attics | Attic Openings | Whole-House Fan | Installation | Sides of fan insulation box assembly will be insulated to the same R-value as adjoining insulated assembly | Insulate to prescribed R-value | Adjudicated - Redline only | 2014-04-22 | 2014-04-22 | John Krigger | Can we really get an R-40 out of movable insulation? I'm assuming that this box assembly is movable insulation but this should be stated. |  |  | Rejected | R-40 of movable insulation is possible; commenter's outcome was unclear | No change | No change | No change
4.1088.1a | Single-Family Homes | Insulation | Attics | Special Considerations | Attic Ventilation | Air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary and thermal boundary Thermal boundary The separation between the interior and exterior environments of a building that slows heat flow | Attic ventilation will be recommended or installed if local code requires attic ventilation during weatherization or retrofits The presence of an effective air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary and thermal boundary Thermal boundary The separation between the interior and exterior environments of a building that slows heat flow between the attic and the living space must be verified and appropriate attic sealing and proper insulation is specified as part of the scope of work | Ensure presence of continuous air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary and thermal boundary Thermal boundary The separation between the interior and exterior environments of a building that slows heat flow | Adjudicated - Redline only | 2014-04-22 | 2014-04-22 | John Krigger | This is one of the details where I don't really understand the trigger. Do you really want a weatherization crew to install more attic ventilation if the attic has only 3/4 of the code-required ventilation? Can air leakage into and out of the attic count? What about climates with humid or very rainy weather is common? When do I need to install more attic ventilation? When is cutting a hole in the roof more of a risk than just leaving an under-ventilated attic alone? |  |  | Rejected | local codes will always supersede prescriptive specifications within program manuals and field guides. If local code requires that additional ventilation be installed in an attic based upon the work being performed then local code shall be followed. | No change | No change | No change
4.1088.8b | Multifamily Homes | Insulation | Attics | Special Considerations | Installation/Correction of Unconditioned Attic Ventilation | Air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary and thermal boundary Thermal boundary The separation between the interior and exterior environments of a building that slows heat flow | Attic ventilation will be recommended or installed only if: The presence of an effective air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary and thermal boundary Thermal boundary The separation between the interior and exterior environments of a building that slows heat flow between the attic and the living space is verified Appropriate attic sealing and proper insulation is specified as part of the work scope Ignition and thermal boundaries are provided when foam plastic materials are used | Ensure presence of continuous air barrier Air barrier The separation between the interior and exterior environments of a building that slows air flow to the point that no smoke movement is visible at 50 pascals of pressure difference across the boundary and thermal boundary Thermal boundary The separation between the interior and exterior environments of a building that slows heat flow | Adjudicated - Redline only | 2014-07-14 | 2014-07-14 | John Krigger | The authors mean barrier not boundary. | Ignition and thermal "barriers" are provided ... |  | Accepted | Clarifies SWS and achieves stated objective. | No change | Attic ventilation will be recommended or installed only if: The presence of an effective air barrier and thermal boundary between the attic and the living space is verified Appropriate attic sealing and proper insulation is specified as part of the work scope Ignition barrier and thermal boundaries are provided when foam plastic materials are used | No change
4.1101.1a | Single-Family Homes | Insulation | Walls | Preparation | Exterior Wall Dense Packing | Preparation | Lead and asbestos safety procedures will be followedCavities will be free of hazards, intact, and able to support dense pack Dense pack The process of installing loose-fill insulation to reduce air flow and perform to a stated R-value pressuresDrilling hazards (e.g., wiring, venting, fuel piping) will be locatedBlocking will be installed around:All openings to inside crawl space and basement for fibrous materialHigh temperature fire-rated materialsWiring and electrical hazardsHeat sourcesAccess to exterior wall cavities will be gained, sheathing will be drilled as needed and probed to locate each cavity, wall studs, and blockersInterior will be masked and dust controlled during drilling when accessing from interiorElectricity supply will be confirmed and will support blowing machine power demandBlowing machine pressure test will be performed with air on full, feed off, agitator running, and gate closedHose outlet pressure will be at least 80 IWC IWC Inches of water column or 2.9 psi Psi Pounds per square inch for cellulose insulation; for other types of dense pack Dense pack The process of installing loose-fill insulation to reduce air flow and perform to a stated R-value insulation, check manufacturer specification for blowing machine set up | Prevent damage to houseProvide a clean work spaceProvide thorough access to allow 100% coverageEnsure proper equipment and process results in consistent densityPrevent settling and retard air flow through cavitiesProtect worker and occupant health | Adjudicated - Redline only | 2014-09-09 | 2014-09-09 | Stephen Lommele | Test justification and substantiation. | Test language. | Test no. | Rejected | Test of system, not comment on SWS. | No change | No change | No change
4.1101.3b | Single-Family Homes | Insulation | Walls | Preparation | Exterior Wall Spray Polyurethane Foam (SPF)&mdash;Masking and Surface Preparation | Substrate repair | Cracks, gaps, and holes in the substrate will be covered or sealed in accordance with manufacturer specifications with appropriate material | Prevent waste of SPF SPF Spray polyurethane foam Prevent overspray into adjacent areas | Adjudicated - Redline only | 2014-04-22 | 2014-04-22 | John Krigger | I don't quite understand what surface we're installing SPF to in this standard. Interior, exterior, open cavity, or to a finished surface? |  |  | Rejected | SWS is clarifying objectives if you are installing SPF on an exterior wall. Auditor will determine which particular surfaces you are applying SPF to, not the SWS. | No change | No change | No change
4.1102.1d | Single-Family Homes | Insulation | Walls | Accessible Walls | Open-Cavity Wall Insulation&mdash;General | Occupant education | A dated receipt signed by the installer will be provided that includes:Insulation typeCoverage areaR-valueInstalled thickness and settled thickness (settled thickness required for loose-fill only)Number of bags installed in accordance with manufacturer specifications (for loose-fill only) | Document job completion to contract specificationsConfirm amount of insulation installedComply with 16 CFR 460.17 | Adjudicated - Redline only | 2014-12-04 | 2014-12-04 | Scott Kashuba | see above | Title "Onsite documentation" | no | Accepted | Clarifies SWS and achieves stated objective. | Onsite documentation | No change | No change
4.1103.1a | Single-Family Homes | Insulation | Walls | Enclosed Walls | Dense Pack Exterior Walls | Exterior dense pack Dense pack The process of installing loose-fill insulation to reduce air flow and perform to a stated R-value | Using fill tube, 100% of each cavity will be filled to a consistent density: Cellulose insulation used in an enclosed cavity will be installed at 3.5 pounds per cubic foot or greater density Blown fiberglass, mineral fiber, or rock and slag wool used in an enclosed cavity will be installed at or above the manufacturer recommended density to limit air flow that corresponds to an air permeance value of 3.5 cfm CFM Cubic feet per minute /sq. ft. at 50 pascals, as measured using BPI BPI Building Performance Institute, www.bpi.org -102 "Standard for Air Resistance of Thermal Insulation Used in Retrofit Cavity Applications – Material Specification" or ASTM ASTM ASTM International, www.astm.org C 522, E 283, or E 2178; the number of bags installed will be confirmed and will match the number required on the coverage chart Insulation will be verified to prevent visible air movement using chemical smoke at 50 pascals of pressure difference | Eliminate voids and settling Minimize framing cavity air flows | Adjudicated - Redline only | 2014-12-15 | 2014-12-15 | Kelly Cutchin C... | The job isn't done until it's patched and cleaned up, so that step should be included here. I don't think it's covered anywhere else in the SWS. | Add a row to this detail describing patching options. We should include something about patching interior walls with plugs/plaster or chair rail trim and patching exterior feed holes with plugs and caulk or siding to keep moisture out. | No, it's already part of the job, just not written down here yet. | Accepted | Clarifies SWS and achieves stated objective. | No change | Using fill tube, 100% of each cavity will be filled to a consistent density: Cellulose insulation used in an enclosed cavity will be installed at 3.5 pounds per cubic foot or greater density Blown fiberglass, mineral fiber, or rock and slag wool used in an enclosed cavity will be installed at or above the manufacturer recommended density to limit air flow that corresponds to an air permeance value of 3.5 cfm /sq. ft. at 50 pascals, as measured using BPI -102 "Standard for Air Resistance of Thermal Insulation Used in Retrofit Cavity Applications – Material Specification" or ASTM C 522, E 283, or E 2178; the number of bags installed will be confirmed and will match the number required on the coverage chart All holes and penetrations will be plugged and/or sealed Insulation will be verified to prevent visible air movement using chemical smoke at 50 pascals of pressure difference | No change
4.1103.2c | Single-Family Homes | Insulation | Walls | Enclosed Walls | Additional Exterior Wall Cavities | Dense packing | Using fill tube, 100% of each cavity will be filled to a consistent density:Cellulose insulation used in an enclosed cavity will be installed at 3.5 pounds per cubic foot or greater densityBlown fiberglass, mineral fiber, or rock and slag wool used in an enclosed cavity will be installed at or above the manufacturer recommended density to limit airflow that corresponds to an air permeance value of 3.5 cfm CFM Cubic feet per minute /sq. ft. at 50 pascals, as measured using BPI BPI Building Performance Institute, www.bpi.org -102 "Standard for Air Resistance of Thermal Insulation Used in Retrofit Cavity Applications—Material Specification" or ASTM ASTM ASTM International, www.astm.org C 522, E 283, or E 2178; the number of bags installed will be confirmed and will match the number required on the coverage chartInsulation will be verified to prevent visible air movement using chemical smoke at 50 pascals of pressure difference | Eliminate voids and settlingMinimize framing cavity air flows | Adjudicated - Redline only | 2015-04-21 | 2015-04-21 | Kelly Cutchin C... | The language isn't related to dense pack, rather the quality control of that dense pack. Belongs in the row below. | Remove this text from the bottom: Insulation will be verified to prevent visible air movement using chemical smoke at 50 pascals of pressure difference. This should be added to the row below for quality control as an either/or option. | No. | Accepted | Clarifies SWS and achieves stated objective. | No change | Using fill tube, 100% of each cavity will be filled to a consistent density: Cellulose insulation used in an enclosed cavity will be installed at 3.5 pounds per cubic foot or greater density Blown fiberglass, mineral fiber, or rock and slag wool used in an enclosed cavity will be installed at or above the manufacturer recommended density to limit airflow that corresponds to an air permeance value of 3.5 cfm /sq. ft. at 50 pascals, as measured using BPI -102 "Standard for Air Resistance of Thermal Insulation Used in Retrofit Cavity Applications—Material Specification" or ASTM C 522, E 283, or E 2178; the number of bags installed will be confirmed and will match the number required on the coverage chart | No change
4.1103.4a | Multifamily Homes | Insulation | Walls | Enclosed Walls | Dense Packing Blown Insulation | Worker safety | All worker safety specifications will be in accordance with SWS 2.0100.3 Worker Safety Lead safety procedures in buildings built before 1980 will be followed | Ensure worker safety, especially in regard to fall protection considerations and contaminants found in demolition, such as asbestos, lead, polychlorinated biphenyls, etc. | Adjudicated - Redline only | 2014-08-05 | 2014-08-05 | Judith Darst | All of our lead safety procedures are based on the year 1978. | Question: Why does this spec (4.1103.4a) refer to 1980: "Lead safety procedures in buildings built before 1980 will be followed?" | No, looking for clarification. | Accepted with modification | Clarifies SWS and achieves stated objective. | No change | All worker safety specifications will be in accordance with SWS 2.0100.3 Worker Safety Lead safety procedures in buildings built before 1978 will be followed, unless approved testing method proves absence of lead based paint in surfaces that will be disturbed | No change
4.1303.1d | Manufactured Housing | Insulation | Floors | Manufactured Housing Floor Cavity Insulation | Insulation of Floor Cavity with Blown Material | Materials | Flame spread index of selected materials will not exceed 25 with an accompanying smoke-developed index not to exceed 450 when tested in accordance with ASTM ASTM ASTM International, www.astm.org E84 or UL UL Underwriters Laboratories 723Flame spread index of foam insulation will not exceed 75 and a smoke- developed index of no more than 450 when tested in the maximum thickness intended for use in accordance with ASTM ASTM ASTM International, www.astm.org E84 or UL UL Underwriters Laboratories 723Foam insulation will be separated from the interior of the building by an approved thermal barrier at a minimum of 1/2" gypsum or a material that is tested in accordance with the acceptance criteria of both the Temperature Transmission Fire Test and the Integrity Fire Test of NFPA NFPA National Fire Protection Association, www.nfpa.org 275Selected material will be of minimal water absorbency Selected material will be noncorrosive | Ensure durability Prevent moisture damage Fire safety will be maintained | Adjudicated - Redline only | 2014-08-05 | 2014-08-05 | Judith Darst | Follow up Questions: Does "Blown Material" refer to cellulose insulation or blown-in foam insulation? If it refers to blown-in foam insulation, then how is that distinguished from "4.1303.3 Insulation of Floor Cavity with Spray Foam Material?" | Question: Why does this spec "4.1303.1 Insulation of Floor Cavity with Blown Material" refer to "Foam insulation?" | No, looking for clarification. | Rejected | The foam insulation referred to is rigid foam board used to repair the belly to prepare it to receive the blown material | No change | No change | No change
4.1401.1a | Single-Family Homes | Insulation | Basements and Crawl Spaces | Band/Rim Joists | Band/Rim Joists&mdash;Spray Polyurethane Foam (SPF) Installation | Preparation | All band/rim joist areas will be open and accessible for SPF SPF Spray polyurethane foam applicationAll surfaces where SPF SPF Spray polyurethane foam is applied will be clean, dry, and free of contamination and degradationSubstrate surfaces will be wiped, blown, or vacuumed to be free of excessive dust and dirtGrease and oil will be removed using appropriate cleaners or solventsMoisture content of all wood substrate materials will be checked to ensure it is below 20% | Prepare all substrate surfaces for the application of SPF SPF Spray polyurethane foam | Adjudicated - Redline only | 2014-07-14 | 2014-07-14 | John Krigger | Using foam board reduces the danger of poisoning by the spray foam because less liquid foam is used. | Include other options such as foam board sealed at the edges with expanding foam. |  | Rejected | This detail specifically addresses those situations where you are using SPF for this application. It is not intended to lay out all options for band/rim joist insulation. 4.1401.2 addresses other options. | No change | No change | No change
4.1401.1b | Single-Family Homes | Insulation | Basements and Crawl Spaces | Band/Rim Joists | Band/Rim Joists&mdash;Spray Polyurethane Foam (SPF) Installation | Installation | SPF SPF Spray polyurethane foam will be applied to desired thickness, using pass thickness maximum in accordance with manufacturer specifications, onto subfloor between floor joists and all rim/band joistsWhen applied to first floor, SPF SPF Spray polyurethane foam will be continuous from subfloor surface, over band/rim joist and sill plate, and in contact with foundation belowWhen applied to second story floor or above, SPF SPF Spray polyurethane foam will be continuous from subfloor surface, over band/rim joist, and in contact with top plate below | Insulate and seal floors | Adjudicated - Redline only | 2014-07-14 | 2014-07-14 | John Krigger | People are assuming from this spec that SPF is the only way to insulate and air-seal a rim joist. You have other standards in the basement wall sections. Should the be moved to this topic or duplicated here? | Move text from other sections or duplicate so people searching for rim joist insulation find it here under this topic. |  | Rejected | 4.1401.2 addresses other options, and is listed in this same subtopic so should be easily found. | No change | No change | No change
4.1401.1b | Single-Family Homes | Insulation | Basements and Crawl Spaces | Band/Rim Joists | Band/Rim Joists&mdash;Spray Polyurethane Foam (SPF) Installation | Installation | SPF SPF Spray polyurethane foam will be applied to desired thickness, using pass thickness maximum in accordance with manufacturer specifications, onto subfloor between floor joists and all rim/band joists When applied to first floor, SPF SPF Spray polyurethane foam will be continuous from subfloor surface, over band/rim joist and sill plate, and in contact with foundation below When applied to second story floor or above, SPF SPF Spray polyurethane foam will be continuous from subfloor surface, over band/rim joist, and in contact with top plate below | Insulate and seal floors | Adjudicated - Redline only | 2015-05-13 | 2015-05-13 | Aaron Travaglini | Line #2 in the above specification is being contradicted in a following specification. the specification is 4.1402.1c. I think there needs to be some review in these 2 areas. | Again I'm not sure how the new text should read. | Not that I know of at this time. | Accepted | Clarifies SWS and achieves stated objective. | No change | SPF will be applied to desired thickness, using pass thickness maximum in accordance with manufacturer specifications, onto subfloor between floor joists and all rim/band joists When applied to first floor, SPF will be continuous from subfloor surface, over band/rim joist and sill plate, and in contact with foundation below, except as stipulated by classification 4.1402.1c When applied to second story floor or above, SPF will be continuous from subfloor surface, over band/rim joist, and in contact with top plate below | No change
4.1401.1c | Single-Family Homes | Insulation | Basements and Crawl Spaces | Band/Rim Joists | Band/Rim Joists&mdash;Spray Polyurethane Foam (SPF) Installation | Fire protection | If SPF SPF Spray polyurethane foam exceeds a thickness of 3", all SPF SPF Spray polyurethane foam will be separated from the occupied interior space of the building with an approved thermal barrier material (typically ½" or thicker gypsum wallboard or an approved thermal barrier coating)Application to rim/band joist up to 3" can be left exposed if the foam is Class I Local codes will be confirmed and followed for fire protection requirements | Provide necessary fire protection for combustible SPF SPF Spray polyurethane foam insulation | Adjudicated - Redline only | 2014-07-13 | 2014-07-13 | John Krigger | Could be confusion between vapor retarder and fire-rated assembly. Also could be interpreted as not requiring a thermal barrier for foam in a habitable space in violation of IRC R312. | Use Class I or Class A fire-rated assembly (not exactly sure of the wording) Class I could be a vapor retarder. Could be confusing. After Class I insert: "unless the space is a habitable space and then cover it with drywall or another thermal barrier." |  | Accepted | Clarifies SWS and achieves stated objective. | No change | If SPF exceeds a thickness of 3", all SPF will be separated from the occupied interior space of the building with an approved thermal barrier material (typically ½" or thicker gypsum wallboard or an approved thermal barrier coating) Application to rim/band joist up to 3" can be left exposed if the foam is Class I, unless the space is a habitable space and then cover it with drywall or another thermal barrier Local codes will be confirmed and followed for fire protection requirements | No change
4.1401.2b | Single-Family Homes | Insulation | Basements and Crawl Spaces | Band/Rim Joists | Band/Rim Joists – Insulation other than Spray Polyurethane Foam | Insulation installation | A foam-based insulation will be installed so as to create a continuous thermal and pressure boundary. If rigid insulation is used, all edges will be sealed and the insulation will be installed tightly to the wood to prevent the movement of moisture throughout the assembly. Insulation will be installed in accordance with local/national code requirements and/or manufacturer’s instructions regarding flame spread. | Improve thermal performance Prevent moisture condensation on the inside of the band joist | Adjudicated - Redline only | 2015-05-29 | 2015-05-29 | Kelly Cutchin C... | The vinyl faced fiberglass batts are often used in commercial basements, and have a standard for vapor permeance - ASTM C665-06 or current, already referenced in SWS. | Add: Or vinyl faced fiberglass batt insulation, installed tightly to the wood and sealed at all edges. | No. | Accepted | Clarifies SWS and achieves stated objective. | No change | A foam-based insulation will be installed so as to create a continuous thermal and pressure boundary or vinyl faced fiberglass batt insulation, installed tightly to the wood and sealed at all edges. If rigid insulation is used, all edges will be sealed and the insulation will be installed tightly to the wood to prevent the movement of moisture throughout the assembly. Insulation will be installed in accordance with local/national code requirements and/or manufacturer’s instructions regarding flame spread | No change
4.1402.1a | Single-Family Homes | Insulation | Basements and Crawl Spaces | Basements and Crawl Space Walls | Closed Crawl Spaces—Wall Insulation | Insulation selection | A non fibrous, fire-rated Class I insulation will be used with a minimum life expectancy of 10 years | Provide fire-safe durable insulation | Adjudicated - Redline only | 2014-03-31 | 2014-07-14 | John Krigger | This spec is vague and misses the main issues of insulating crawl space walls. What do you mean by non-absorbent and fire rated? Does non-absorbent mean no fibrous insulation: That wouldn't be a bad decision. Fiberglass only absorbs 7% water by weight but the common facings used in crawl spaces are vapor barriers, which hinder drying. Fiberglass batts aren't a bad choice for dry climates: suggest < 20 inches of precip and <60% average rh. However, the vapor-barrier facing is still a problem. I think that by fire-rated you mean 25 or less flame spread or Class I or Class A rating. Might as well mention all of these ratings. | n/a |  | Accepted | Clarifies SWS and achieves stated objective. | No change | A fire-rated insulation (25 or less flame spread or Class I or Class A) will be used with a minimum life expectancy of 10 years | Provide fire-safe, durable insulation that will not exacerbate moisture issues in the crawl space
4.1402.1a | Single-Family Homes | Insulation | Basements and Crawl Spaces | Basements and Crawl Space Walls | Closed Crawl Spaces—Wall Insulation | Insulation selection | A non fibrous, fire-rated Class I insulation will be used with a minimum life expectancy of 10 years | Provide fire-safe durable insulation | Adjudicated - Redline only | 2015-04-03 | 2015-04-03 | Kelly Cutchin C... | Last review session, I believe the language was updated to specify non-fibrous insulation. Moisture concerns led to this update but the objective was not updated. It can currently be argued that fibrous insulations meet the stated objective. | Update objectives to read: Provide fire-safe, durable insulation that will not exacerbate moisture issues in the crawl space. | Yes. Foam board is typically more expensive than batt fiberglass insulation. This was deemed acceptable in the previous update when "non-fibrous" was adopted. | Accepted | Clarifies SWS and achieves stated objective. | No change | No change | Provide fire-safe, durable insulation that will not exacerbate moisture issues in the crawl space
4.1402.1c | Single-Family Homes | Insulation | Basements and Crawl Spaces | Basements and Crawl Space Walls | Closed Crawl Spaces—Wall Insulation | Termite inspection gap | Where termite pressure exists, a 3" inspection gap will be maintained from the top of the insulation to the bottom of any wood | Allow for termite detection | Adjudicated - Redline only | 2015-05-13 | 2015-05-13 | Aaron Travaglini | I am just trying to get clarification on the above specification. There is no location to actually voice concerns or complaints. | Can you please explain what the term "termite pressure" means. If the crawlspace is intended to be insulated and air sealed how does this inspection gap help? The sill plate and foundation wall are not sealed and need to be treated. Applying urethane foam from the upper floor of the box sill down over the sill plate and continuing onto the foundation wall to create a monolithic surface is the most common practice. | The specification above is the reason the cost of installation/implementation has gone up. It is more cumbersome to treat the area now then it ever has been in the past. The main reason for the increase is the area still needs to be air sealed. We are exploring other ways to treat the area but reverting back to urethane foam over the entire area will be the easier solution. | Rejected | Termite issues vary vastly across the nation and this policy must encompass those areas | No change | No change | No change
4.1402.1d | Single-Family Homes | Insulation | Basements and Crawl Spaces | Basements and Crawl Space Walls | Closed Crawl Spaces—Wall Insulation | Attachment | Insulation will be attached with a durable connection equal to or better than manufacturer specifications | Prevent insulation from detaching from the foundation wall | Adjudicated - Redline only | 2014-07-14 | 2014-07-14 | John Krigger | Confusing and redundant wording | Insulation will be attached with a durable connection better than or equal to manufacturer specifications. |  | Accepted | Clarifies SWS and achieves stated objective. | No change | Insulation will be attached with a durable connection better than or equal to manufacturer specifications | No change
4.1402.2c | Single-Family Homes | Insulation | Basements and Crawl Spaces | Basements and Crawl Space Walls | Basement Wall Insulation&mdash;No Groundwater Leakage | Vapor permeability | When absorbent insulation materials are installed, assembly will remain vapor permeable to the interior in all climate zones except Zone 7 | Provide drying potential to the basement | Adjudicated - Redline only | 2014-07-13 | 2014-07-13 | John Krigger | Current standard all but bans foundation insulation. | Oops, I was being too optimistic in my previous comment. You would have to change "vapor permeable" to vapor "semi-impermeable" meaning Class II vapor retarder to allow the most common insulation assemblies for foundation walls. |  | Accepted | Clarifies SWS and achieves stated objective. | No change | When absorbent insulation materials are installed, assembly will remain vapor semi-impermeable to the interior in all climate zones except Zone 7 | No change
4.1402.2c | Single-Family Homes | Insulation | Basements and Crawl Spaces | Basements and Crawl Space Walls | Basement Wall Insulation&mdash;No Groundwater Leakage | Vapor permeability | When absorbent insulation materials are installed, assembly will remain vapor permeable to the interior in all climate zones except Zone 7 | Provide drying potential to the basement | Adjudicated - Redline only | 2014-07-13 | 2014-07-13 | John Krigger | Current standard all but forbids basement and crawl-space wall insulation. Vapor permeable means more than 10 perms according to ASHRAE. Unfaced fiberglass or spray fiber would be the only common insulations that would comply and they aren't durable. | Instead of "vapor permeable" insert "vapor semi-permeable". |  | Accepted | Clarifies SWS and achieves stated objective. | No change | When absorbent insulation materials are installed, assembly will remain vapor semi-impermeable to the interior in all climate zones except Zone 7 | No change
5.3003.14a | Single-Family Homes, Manufactured Housing | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Gas-Fired Appliances (LP and Natural Gas) | Place appliance in operation | Heating equipment will be placed in operation in accordance with applicable NFPA NFPA National Fire Protection Association, www.nfpa.org standards and manufacturer specifications when available | Ensure equipment: Operates as designed Operates safely Operates efficiently Is durable | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | This isn't replacement, it's evaluating existing units, right? | will be evaluated |  | Rejected | The phrasing "Place in operation" means the unit will be turned on, which is a step in overall evaluation. | No change | No change | No change
5.3003.14b | Single-Family Homes, Manufactured Housing | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Gas-Fired Appliances (LP and Natural Gas) | Gas pressure | Measurement will be verified by a certified professional in accordance with fuel type and manufacturer specifications | Ensure equipment: Operates as designed Operates safely Operates efficiently Is durable | Adjudicated - Redline only | 2015-02-16 | 2015-02-16 | John Krigger | If CO, oxygen, and gas temperature are good, I see no reason to require gas pressure measurement. Gas pressure can be in a wide range 3.2-4.5 or something like that. Clocking the meter might be necessary to discover the cause of too high or too low flue gas temperature but you couldn't learn much from gas pressure alone. | Determine the gas BTUH input by clocking the gas meter if necessary to diagnose problems with CO, flue-gas temperature, or oxygen content. |  | Accepted with modification | Measuring the gas pressure must be done by a certified professional (as stated). This should be part of an overall tuneup. | No change | If fault has been determined in the preceding steps, then measurement will be verified by a certified professional in accordance with fuel type and manufacturer specifications (move spec down to a lower number) | No change
5.3003.14e | Single-Family Homes, Manufactured Housing | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Gas-Fired Appliances (LP and Natural Gas) | Carbon monoxide ( CO CO Carbon monoxide ) in flue gas | CO CO Carbon monoxide in the undiluted flue gas will be less than 100 ppm | Ensure equipment: Operates as designed Operates safely Operates efficiently Is durable | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | This is a clear mistake or an unacceptable duality given the 200/400 ppm standard in health and safety. | Is it 100 or 200??? |  | Accepted with modification | Align with BPI 1200 | No change | CO in the undiluted flue gas will be less than 400 ppm air-free | No change
5.3003.14e | Single-Family Homes, Manufactured Housing | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Gas-Fired Appliances (LP and Natural Gas) | Carbon monoxide ( CO CO Carbon monoxide ) in flue gas | CO CO Carbon monoxide in the undiluted flue gas will be less than 100 ppm | Ensure equipment: Operates as designed Operates safely Operates efficiently Is durable | Adjudicated - Redline only | 2014-12-19 | 2014-12-19 | Kelly Cutchin C... | As measured and air free readings give different CO levels for the same conditions, so we need to state which measurement is meant. | Clarify if the 100 ppm limit is as measured or air free. | No. | Accepted with modification | Align with BPI 1200 | No change | CO in the undiluted flue gas will be less than 400 ppm air-free | No change
5.3003.14f | Single-Family Homes, Manufactured Housing | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Gas-Fired Appliances (LP and Natural Gas) | Testing/inspection holes | All testing and inspection holes will be sealed with manufacturer approved materials | Ensure equipment: Operates as designed Operates safely Operates efficiently Is durable | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | Too vague to be useful. | Would need considerable additional language. |  | Rejected | The SWS spec is to seal holes with appropriate materials. This can be confirmed by inspection. | No change | No change | No change
5.3003.15h | Manufactured Housing | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Oil-Fired Appliances | Excess combustion air | Excess combustion air will be calculated and shown to be in accordance with industry manuals (e.g., Testo, Bacharach) | Ensure equipment: Operates as designed Operates safely Operates efficiently Is durable | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | Industry manuals: what do you mean? A lot of equipment specs don't include SSE, O2, flue gas temp. | Accepted standards?? Why don't you suggest some? |  | Accepted with modification | Users of the SWS are not expected to be qualified to act upon adjustments of efficiency. This should be part of a general tune-up. | No change | Excess air will be minimized in accordance with industry best practices | No change
5.3003.15i | Manufactured Housing | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Oil-Fired Appliances | CO CO Carbon monoxide in flue gas | CO CO Carbon monoxide in the undiluted flue gas will be less than 100 ppm | Ensure equipment: Operates as designed Operates safely Operates efficiently Is durable | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | I can't justify having 100 ppm here with mostly sealed-combustion appliances (mobile home) when you spec 200 for open-combustion in site-built homes. | 100/200 dilemma continued. |  | Accepted with modification | Align with BPI 1200 | No change | CO in the undiluted flue gas will be less than 400 ppm air-free | No change
5.3003.15i | Manufactured Housing | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Oil-Fired Appliances | CO CO Carbon monoxide in flue gas |  |  | Adjudicated - Redline only | 2015-12-15 | 2015-12-15 | Kelly Cutchin C... | Align with BPI 1200. Note - This is already in the table of comments to be sent to committee. It should be pulled out and addressed along with the combustion safety updates. | CO in the undiluted flue gas will be less than 400 ppm air free. |  | Accepted with modification | This comment has been addressed in the Combustion Safety REDLINE document on the SWS Maintenance Page (https://sws.nrel.gov/maintenance): The document has been updated to "400 ppm air-free" to align with BPI 1200. In addition, this same language was updated in 5.3003.14e, for both single family and manufactured housing.
5.3003.2a | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Oil-Fired Appliances | Oil system: nozzle size | Nozzle size will be correct for design input and within equipment firing rate of the heating system manufacturer | Ensure equipment operates as designed Ensure equipment operates safely Ensure equipment operates efficientlyEnsure equipment is durable | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | Be consistent. | Combine single-family with mobile with tabs. Confusing as is given your convention of using tabs. Allows for comparison. |  | Further investigation required | No language change - add tab for to 5.3003.15 forMH Two issues: 1. checking the nozzle size is not expected from the users of the SWS. 2. Commenter has a good point about the lack of a tab for MH unless there are never oil burners in manufactured homes. | No change | No change | No change
5.3003.2a | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Oil-Fired Appliances | Oil system: nozzle size | Nozzle size will be correct for design input and within equipment firing rate of the heating system manufacturer | Ensure equipment operates as designed Ensure equipment operates safely Ensure equipment operates efficientlyEnsure equipment is durable | Adjudicated - Redline only | 2016-07-27 | 2016-07-27 | Charles Kurnik | Under committee guidance, this entire Detail has been reorganized to reflect the order in which the work should occur, and to reference ACCA 5.Additional Specification rows have also been added. | New text to be provided in 2016 redline version |  | Accepted | Added new specification to clarify | Oil System: filter | Filter will be present, clean, and leak free | Ensure oil filter is present and functional
5.3003.2d | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Oil-Fired Appliances | Oil system: smoke test (This test must be conducted before any combustion testing is completed) | Smoke spot reading will be in accordance with burner manufacturer specificationsIf smoke test is more than actionable levels, specify a clean and tune | Ensure equipment operates as designed Ensure equipment operates safely Ensure equipment operates efficientlyEnsure equipment is durable | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | Current standard too vague to be useful or credible. | Smoke spot should be less than 1. |  | Rejected | Intent of SWS is for smoke spot to be in accordance with burner manufacturer specifications | No change | No change | No change
5.3003.2d | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Oil-Fired Appliances | Oil system: smoke test (This test must be conducted before any combustion testing is completed) | Smoke spot reading will be in accordance with burner manufacturer specificationsIf smoke test is more than actionable levels, specify a clean and tune | Ensure equipment operates as designed Ensure equipment operates safely Ensure equipment operates efficientlyEnsure equipment is durable | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | Do this before taking steady-state efficiency. | Place before current 2c |  | Accepted with modification | No language change - switch order with 5.3003.2c Number of issues here: No comment was made on 5.3003.2b regarding a measurement of oil pressure which is not expected from users and probably should be removed; Second, commenter has a point that the smoke spot test should be done before SSE especially if 5.3003.2d is going to remain in place. | No change | No change | No change
5.3003.2f | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Oil-Fired Appliances | Carbon dioxide and oxygen | Measurement will be verified in accordance with industry manuals and manufacturer specifications | Ensure equipment operates as designed Ensure equipment operates safely Ensure equipment operates efficientlyEnsure equipment is durable | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | I believe that all current testers measure oxygen. Why mention CO2? Steady-state efficiency handles this anyway. | If steady-state is out of range, notice the O2 reading to see if it is high or low. |  | Rejected | Not enough detail in comment, please clarify | No change | No change | No change
5.3003.2g | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Oil-Fired Appliances | Excess air | Excess air will be calculated and shown to be in accordance with manufacturer specifications | Ensure equipment operates as designed Ensure equipment operates safely Ensure equipment operates efficientlyEnsure equipment is durable | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | Delete standard. It is redundant with previous mentioning O2. | Delete, if you analyze O2 it is the same as analyzing excess air. |  | Accepted with modification | Language changed to clarify SWS and achieves stated objective. | No change | Excess air will be minimized in accordance with industry best practices | No change
5.3003.2h | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Combustion Analysis of Oil-Fired Appliances | CO CO Carbon monoxide in flue gas | Undiluted flue gases will be checked with a calibrated combustion analyzerFor CO CO Carbon monoxide levels exceeding 200 ppm as measured, or 400 ppm air-free measurement, service will be provided to reduce CO CO Carbon monoxide to below these levels (unless CO CO Carbon monoxide measurement is within manufacturer specifications) | Ensure equipment operates as designed Ensure equipment operates safely Ensure equipment operates efficientlyEnsure equipment is durable | Adjudicated - Redline only | 2014-09-02 | 2014-09-02 | John Krigger | Oil is usually adjustable to below 100 ppm and the argument is good for doing so. Less soot. | Make up your mind about 100/200 ppm |  | Accepted with modification | Adjust the levels to align with BPI 1200 | No change | Undiluted flue gases will be checked with a calibrated combustion analyzer For CO levels exceeding 400 ppm air-free measurement, service will be provided to reduce CO to below these levels (unless CO measurement is within manufacturer specifications). Adjustment to achieve CO reading of less than 200 air-free shall be attempted | Ensure equipment operates as designed Ensure equipment operates safely Ensure equipment operates efficientlyEnsure equipment is durable Reduce soot.
5.3003.3a | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Evaluating Air Flow | Total air flow | Total system air flow will be measured by:Temperature riseFlow plateFan depressurization device (e.g., Duct Blaster, DucTester) | Ensure equipment operates as designed Ensure equipment operates efficiently Ensure equipment provides comfort Ensure equipment operates safely Ensure equipment is durable | Adjudicated - Redline only | 2014-04-23 | 2014-04-23 | Darrel Tenter Tenter | Duct Blaster and DucTester are both registered trademarks and should bear the ® symbol when used. |  |  | Accepted with modification | Trademarks are important to protect. | No change | Total system air flow will be measured by one of the following methods: Temperature riseFlow plateFan depressurization device (e.g., Duct Blaster®, DucTester®) | No change
5.3003.3a | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Evaluating Air Flow | Total air flow | Total system air flow will be measured by:Temperature riseFlow plateFan depressurization device (e.g., Duct Blaster, DucTester) | Ensure equipment operates as designed Ensure equipment operates efficiently Ensure equipment provides comfort Ensure equipment operates safely Ensure equipment is durable | Adjudicated - Redline only | 2015-06-03 | 2015-06-03 | Kelly Cutchin C... | All 3 measurements aren't required to meet the stated objectives, but as written the SWS could be interpreted to mean you must do all 3 tests. | Total system air flow will be measured by one of the following methods: | No. | Accept | Clarifies SWS and achieves stated objective. | No change | Total system air flow will be measured by one of the following methods: Temperature riseFlow plateFan depressurization device (e.g., Duct Blaster®, DucTester®) | No change
5.3003.5a | Manufactured Housing | Heating and Cooling | Forced Air | System Assessment and Maintenance | Refrigerant Line Inspection | Insulation | All liquid refrigerant lines will be insulated to a minimum of R-4Vapor or high side lines will not be insulated unless specified by the equipment's manufacturerSuction lines will be insulated to a minimum of R-4For mixed humid, hot humid, and marine climates, heating and cooling refrigerant lines will be insulated | Ensure refrigerant lines do not gain excessive heatPrevent energy loss and condensation | Adjudicated - Redline only | 2015-08-10 | 2015-08-10 | CHP Energy Solutions | The liquid refrigerant line is the the high side (small tube) which is usually warm since it is under pressure and a high temp liquid. The original specification indicates that the vapor line is the high-side line, which is entirely incorrect. The spec also, by mistakenly calling for the liquid and suction lines to be insulated, calls for both lines in the set to be insulated. This clarification is needed to make sure that insulation is not being installed where it doesn't need to be. The objective change is to reflect the actual reason for insulating the suction line which is to prevent condensation from occurring inside the building cavities on the exterior surfaces of the cold vapor line. This is because with the above adjustments the proper lines will already be insulated and this additional sentence is unnecessary and creates the debate over what climate zone you are "really" in. The reference to the manufacturer's instructions will make sure the high side line is insulated when necessary. | Remove the requirement that "all liquid refrigerant lines will be insulated to a minimum of R4" since only the Suction line (low pressure, vapor line) must be insulated unless the manufacturer calls for it. The new spec should read: "All suction or vapor refrigerant lines, will be insulated to a minimum of R-4" "High-side or liquid refrigerant lines will not be insulated unless specified by the equipment's manufacturer" The objective should also be changed to indicate that this is to prevent condensation from the vapor line. It should now read: "Ensure refrigerant lines do not gain excessive heat, or cause condensation to occur inside the building envelope" Also remove the last sentence about mixed humid, hot humid, and marine climates.... | No cost increase is expected. It may lead to a reduction in cost, as the spec is currently calling for both lines to be insulated. | Accept | Clarifies SWS and achieves stated objective. | No change | All suction or vapor refrigerant lines, will be insulated to a minimum of R-4 High-side or liquid refrigerant lines will not be insulated unless specified by the equipment's manufacturer | Ensure refrigerant lines do not gain excessive heat, or cause condensation to occur inside the building envelope
5.3003.5a | Single-Family Homes | Heating and Cooling | Forced Air | System Assessment and Maintenance | Refrigerant Line Inspection | Insulation | All liquid refrigerant lines will be insulated to a minimum of R-4Vapor or high side lines will not be insulated unless specified by the equipment's manufacturerSuction lines will be insulated to a minimum of R-4 | Ensure refrigerant lines do not gain excessive heat | Adjudicated - Redline only | 2015-08-10 | 2015-08-10 | CHP Energy Solutions | The liquid refrigerant line is the the high side (small tube) which is usually warm since it is under pressure and a high temp liquid. The original specification indicates that the vapor line is the high-side line, which is entirely incorrect. The spec also, by mistakenly calling for the liquid and suction lines to be insulated, calls for both lines in the set to be insulated. This clarification is needed to make sure that insulation is not being installed where it doesn't need to be. The objective change is to reflect the actual reason for insulating the suction line which is to prevent condensation from occurring inside the building cavities on the exterior surfaces of the cold vapor line. | Remove the requirement that "all liquid refrigerant lines will be insulated to a minimum of R4" since only the Suction line (low pressure, vapor line) must be insulated unless the manufacturer calls for it. The new spec should read: "All suction or vapor refrigerant lines, will be insulated to a minimum of R-4" "High-side or liquid refrigerant lines will not be insulated unless specified by the equipment's manufacturer" The objective should also be changed to indicate that this is to prevent condensation from the vapor line. It should now read: "Ensure refrigerant lines do not gain excessive heat, or cause condensation to occur inside the building envelope" | No cost increase is expected. It may lead to a reduction in cost, as the spec is currently calling for both lines to be insulated. | Rejected (duplicate) | Duplicate comment, previosuly accepted | No change | No change | No change
5.3102.1a | Multifamily Homes | Heating and Cooling | Hydronic Heating (Hot Water and Steam) | Equipment Installation | Replacement with Hot Water Boiler | Assessment | Confirmation of the scope of work will be made for the following: ClearancesProper drainage in boiler roomFlue/chimney conditionsElectrical capacityOil/gas availabilityPiping connections | Verify scope of work | Adjudicated - Redline only | 2014-06-03 | 2014-06-03 | Juan Saiz | Tested co after water heart was install reading were 0 and reading tape will be attacted with the report |  |  | Rejected | Not enough detail in comment, please clarify | No change | No change | No change
5.3104.2f | Single-Family Homes | Heating and Cooling | Hydronic Heating (Hot Water and Steam) | Equipment Maintenance, Testing, and Repair | Maintenance: Gas Boiler Service Inspection | Flue gas testing | Undiluted flue gases will be checked with a calibrated combustion analyzer in accordance with BPI BPI Building Performance Institute, www.bpi.org -1100-T-2012If combustion is not in compliance with BPI BPI Building Performance Institute, www.bpi.org -1100-T-2012, diagnostics and adjustments will be done to meet manufacturer specifications or local codes | Confirm that combustion occurs safely with maximum efficiency | Adjudicated - Redline only | 2013-04-01 | 2014-07-14 | Thom Knoll | At 5.3104.2f Flue Gas Testing, references compliance with BPI-1100-T-2012, but the referenced Home Energy Audit Standard does not seem to have any description or limit for undiluted flue gas content (or whatever else was supposed to be at this reference). | n/a |  | Accepted with modification | Spec will now refer to BPI 1200 | No change | Undiluted flue gases will be checked with a calibrated combustion analyzer in accordance with BPI 1200 or other approved standard If combustion is not in compliance with the referenced standard, diagnostics and adjustments will be referred to a qualified technician to meet manufacturer specifications or local codes | No change
6.6004.2g | Multifamily Homes | Ventilation | Exhaust | Exhaust Ventilation Systems | Individual Exhaust Fan Serving Multiple Rooms Within Single Dwelling Unit (All Building Types) | Backdraft dampers (required in intermittent systems) | A backdraft damper Backdraft damper A damper that allows air to flow in only one direction will be installed between the fan and the exterior unless the system operates continuously A backdraft damper Backdraft damper A damper that allows air to flow in only one direction will be installed in any duct serving any room with a separate exhaust (e.g., dryer) | Prevent reverse air flow when the system is offPrevent spread of contaminants between rooms | Adjudicated - Redline only | 2014-09-08 | 2014-09-08 | Steve Divan | Any ASHRAE fan is required to allow the occupant to be able to disable the fan. Even if a fan is intended to be used continuously, if it can be turned off then isn't a damper needed to prevent infiltration/exfiltration? | A Backdraft damper will be installed between the fan and the exterior. | No. ll fans I am aware of come with backdraft dampers, there should be no increase in cost. | Accepted | Clarifies SWS and achieves stated objective. | No change | A backdraft damper will be installed between the fan and the exterior A backdraft damper will be installed in any duct serving any room with a separate exhaust (e.g., dryer) | No change
6.6102.3a | Single-Family Homes | Ventilation | Supply | Components | Intake for Ventilation Air to Forced Air System Used for Heating or Cooling | Forced air system requirements | Existing forced air system leakage to outside will be less than 10% of the air handler flow when measured at 25 pascals with reference to outsideAny portion of the return located inside the combustion applianceZone will be air sealed | Reduce migration of pollutants | Adjudicated - Redline only | 2014-12-18 | 2014-12-18 | Kelly Cutchin C... | It appears this is an unfinished sentence. Not sure what is meant. | Clarify what is meant by second bullet item: Any portion of the return located inside the combustion appliance | No. | Accepted | Clarifies SWS and achieves stated objective. | No change | Existing forced air system leakage to outside will be less than 10% of the air handler flow when measured at 25 pascals with reference to outside Any portion of the return located inside the combustion appliance zone will be air sealed | No change
6.6201.1a | Single-Family Homes | Ventilation | Whole Building Ventilation | Air Flow Requirements | Installed System Air Flow | Separate exhaust for all baths and kitchens plus primary ventilation | Air flows will be measured and adjusted to meet the current version of ASHRAE ASHRAE American Society of Heating, Refrigerating and Air-Conditioning Engineers, www.ashrae.org 62.2 and in compliance with the authority having jurisdiction. See Calculation of the Infiltration Credit for calculation information and examples | Provide sufficient flows in accordance with current ventilation standards | Adjudicated - Redline only | 2014-04-23 | 2014-04-23 | Darrel Tenter Tenter | Insert space or line return before "For intermittent..." in last sentence. |  |  | Rejected | Language no longer in SWS | No change | No change | No change
6.6201.1a | Single-Family Homes | Ventilation | Whole Building Ventilation | Air Flow Requirements | Installed System Air Flow | Separate exhaust for all baths and kitchens plus primary ventilation | Air flows will be measured and adjusted to meet the current version of ASHRAE 62.2 and in compliance with the authority having jurisdiction. See Calculation of the Infiltration Credit for calculation information and examples | Provide sufficient flows in accordance with current ventilation standards | Adjudicated - Redline only | 2014-12-18 | 2014-12-18 | Kelly Cutchin C... | The language here is repeated in next row. Remove this row. | NA - remove this row, as it is repetitive with next row of this detail. | No. | Accepted with modification | Rewritten by committee and merged with Detail 6.6204.4 MH; Detail number 6.6202.1 will be deleted | Delete | Delete | Delete
6.6201.1b | Single-Family Homes | Ventilation | Whole Building Ventilation | Air Flow Requirements | Installed System Air Flow | Separate exhaust for all baths and kitchens sufficient to meet primary ventilation requirements | Air flows will be measured and adjusted to meet the current version of ASHRAE 62.2 and in compliance with the authority having jurisdiction. See Calculation of the Infiltration Credit for calculation information and examples | Provide sufficient flows per current ventilation standards | Adjudicated - Redline only | [6 empty] | Accepted with modification | Rewritten by committee and merged with Detail 6.6204.4 MH; Detail number 6.6202.1 will be deleted | Delete | Delete | Delete
6.6201.1c | Single-Family Homes | Ventilation | Whole Building Ventilation | Air Flow Requirements | Installed System Air Flow | Single additional fan to meet all ventilation requirements | Air flows will be measured and adjusted to meet the current version of ASHRAE 62.2 and in compliance with the authority having jurisdiction. See Calculation of the Infiltration Credit for calculation information and examples | Provide sufficient flows in accordance with current ventilation standards | Adjudicated - Redline only | [6 empty] | Accepted with modification | Rewritten by committee and merged with Detail 6.6204.4 MH; Detail number 6.6202.1 will be deleted | Delete | Delete | Delete
6.6202.3b | Multifamily Homes | Ventilation | Whole Building Ventilation | Components | Airflow Control Devices (All Building Types) | Preparation | Duct cleaning will be performed in compliance with ANSI ANSI American National Standards Institute, www.ansi.org / ACCA ACCA Air Conditioning Contractors of America, www.acca.org 6 HVAC HVAC Heating, ventilation, and air conditioning System Cleanliness-2007Register cleaning or replacement will be performed as specifiedDuct sealing will be performed as specifiedStack pressures will be verified for proper operation of flow control devicePresence and type of dampers and smoke control devices will be identified, and installer will ensure the installation of the air flow device will not interfere with proper operation | Establish preconditions for installing flow control deviceEnsure health and safety of occupant | Adjudicated - Redline only | 2014-12-03 | 2014-12-03 | Jim Harmon Harmon | Obviously duct cleaning is not required for all whole-building ventilation systems encountered by home performance/ Wx/ HVAC professionals. However, this spec could be misinterpreted as requiring duct cleaning as a preparation for all buildings/ systems. Please clarify verbiage. | Duct cleaning, when performed, will be performed in compliance with ANSI / ACCA 6 HVAC System Cleanliness-2007 | No; to the contrary. | Accepted | Clarifies SWS and achieves stated objective. | No change | Duct cleaning, when performed, will be performed in compliance with ANSI / ACCA 6 HVAC System Cleanliness-2007 Register cleaning or replacement will be performed as specified Duct sealing will be performed as specified Stack pressures will be verified for proper operation of flow control device Presence and type of dampers and smoke control devices will be identified, and installer will ensure the installation of the air flow device will not interfere with proper operation | No change
6.6202.9b | Multifamily Homes | Ventilation | Whole Building Ventilation | Components | Filtration for Fan-Powered (Active) Systems | Selection | All mechanically supplied outdoor air will pass through filter before conditioningFilters and filter racks/holders will have a rating of minimum efficiency rating value 6 or higher when tested in accordance with ASHRAE ASHRAE American Society of Heating, Refrigerating and Air-Conditioning Engineers, www.ashrae.org 52.2-2007Pressure drop across filter will match equipment capabilitiesFilter systems that produce ozone will not be allowed | Ensure outdoor air is filtered before entering occupied spaceEnsure occupant health and safety | Adjudicated - Redline only | 2014-04-22 | 2014-04-22 | Steve Divan | This should be included under single family and manufactured homes also. Systems that supply outside air can also be installed in those types of .housing |  |  | Accepted with modification | Add entire detail (6.6202.9) to SF and MH library. Remove year from 52.2 standard | No change | All mechanically supplied outdoor air will pass through filter before conditioningFilters and filter racks/holders will have a rating of minimum efficiency rating value 6 or higher when tested in accordance with ASHRAE 52.2 Pressure drop across filter will match equipment capabilities Filter systems that produce ozone will not be allowed | No change
6.6202.9b | Multifamily Homes | Ventilation | Whole Building Ventilation | Components | Filtration for Fan-Powered (Active) Systems | Selection | All mechanically supplied outdoor air will pass through filter before conditioningFilters and filter racks/holders will have a rating of minimum efficiency rating value 6 or higher when tested in accordance with ASHRAE ASHRAE American Society of Heating, Refrigerating and Air-Conditioning Engineers, www.ashrae.org 52.2-2007Pressure drop across filter will match equipment capabilitiesFilter systems that produce ozone will not be allowed | Ensure outdoor air is filtered before entering occupied spaceEnsure occupant health and safety | Adjudicated - Redline only | 2014-04-27 | 2014-04-27 | Steve Divan | It seems that this could apply to single family homes also. An HRV or ERV is occasionally installed in a single family home. I would think the filtration requirement would apply in those cases. |  |  | Accepted | Add entire detail (6.6202.9) to SF and MH library | No change | No Change | No change
6.6204.1a | Manufactured Housing | Ventilation | Whole Building Ventilation | Equipment Evaluation | Commissioning Existing Exhaust or Supply Ventilation Systems | Systems check | Visual inspection will be performed and documented for: Electrical connections Name plate (rated sone and flow) Damper operation (internal and external) Motor cleanlinessDucts: Connections (proper materials, sealed and connected) Insulation Support Sizing Termination | Evaluate systems | Adjudicated - Redline only | 2016-07-26 | 2016-07-26 | Charles Kurnik | Under committee guidance, The Detail 6.6204.1 is being rewritten to apply to single family and manufactured housing. 6.6201.1 is being deleted and incorporated into this rewrite. | Text to come. |  | Accepted | Language and changes proposed by committee: • Change Subtopic to "System Evaluation" • Change Detail name to "Commisioning Ventilation System" • Add detail to single-family homes in addition to manufactured housing | Identification | Identify whole building ventilation strategy that was installed in the home, based on options described in current version of ASHRAE 62.2, e.g., exhaust only, supply only, balanced, combining local and whole home ventilation delivery, incorporating infiltration credit, etc. | Ensure suitable whole building ventilation strategy is installed Identify testing requirements to determine installed system air flow
6.6204.1b | Manufactured Housing | Ventilation | Whole Building Ventilation | Equipment Evaluation | Commissioning Existing Exhaust or Supply Ventilation Systems | Verify flow rate | Calibrated device will be used to test for flow measurement | Ensure proper flow | Adjudicated - Redline only | N/A | N/A | N/A | N/A | N/A | N/A | Accepted | Language and changes proposed by committee: • Change Subtopic to "System Evaluation" • Change Detail name to "Commisioning Ventilation System" • Add detail to single-family homes in addition to manufactured housing | Equipment inspection | Visually inspect and document status of: · Electrical connections · Name plate (rated sone and flow) · Motor cleanliness | Evaluate equipment
6.6204.1c | Manufactured Housing | Ventilation | Whole Building Ventilation | Equipment Evaluation | Commissioning Existing Exhaust or Supply Ventilation Systems | Work order | Work order will be developed as necessary in accordance with systems check and flow rate | Correct deficiencies Ensure proper operation | Adjudicated - Redline only | N/A | N/A | N/A | N/A | N/A | N/A | Accepted | Language and changes proposed by committee: • Change Subtopic to "System Evaluation" • Change Detail name to "Commisioning Ventilation System" • Add detail to single-family homes in addition to manufactured housing | Pathway inspection | Visually inspect and document status of ducting or other airflow pathways to ensure proper: · Connections (proper materials, sealed and connected) · Insulation · Support · Sizing, and · Termination locations and fittings Verify proper damper operation | Preserve integrity of building envelope Effectively move air along selected pathways
6.6204.1d | Manufactured Housing | Ventilation | Whole Building Ventilation | Equipment Evaluation | Commissioning Existing Exhaust or Supply Ventilation Systems | Total ventilation airflow | Total exhaust and/or supply system ventilation airflow will be measured | Ensure airflow is as designed | Adjudicated - Redline only | N/A | N/A | N/A | N/A | N/A | N/A | Accepted | Language and changes proposed by committee: • Change Subtopic to "System Evaluation" • Change Detail name to "Commisioning Ventilation System" • Add detail to single-family homes in addition to manufactured housing | Measurement and Adjustment | Using a calibrated device, measure air flow of all necessary components, including building air leakage when relevant Adjust ventilation equipment air flows as necessary to meet the ventilation rates required by the current version of ASHRAE 62.2. | Provide sufficient air flows per current ventilation standards Verify suitable performance of installed ventilation strategy
6.6204.1e | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Adjudicated - Redline only | N/A | N/A | N/A | N/A | N/A | N/A | Accepted | New Spec Language and changes proposed by committee: • Change Subtopic to "System Evaluation" • Change Detail name to "Commisioning Ventilation System" • Add detail to single-family homes in addition to manufactured housing | Work order | Develop work order as necessary to correct deficiencies identified during inspections and measurement. | Correct deficiencies Ensure proper operation
6.6204.1f | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Adjudicated - Redline only | N/A | N/A | N/A | N/A | N/A | N/A | Accepted | New Spec Language and changes proposed by committee: • Change Subtopic to "System Evaluation" • Change Detail name to "Commisioning Ventilation System" • Add detail to single-family homes in addition to manufactured housing | Occupant education | Instruct occupant on purpose, use and maintenance of ventilation, and typical signs that ventilation is needed, e.g., condensation on windows. | Occupant understands benefits of good indoor air quality and can operate ventilation equipment as needed.
6.6205.1c | Manufactured Housing | Ventilation | Whole Building Ventilation | Exhaust-Only System | Manufactured Housing Exhaust-Only Strategies | Location | No resistance greater than 3 pascals will exist between fan intake location with reference to the common areaExhaust ventilation for common spaces will not be installed in bathrooms or bedrooms | Ensure fresh air distribution to common areas | Adjudicated - Redline only | 2014-04-22 | 2014-04-22 | Steve Divan | The comment that exhaust ventilation for common spaces will not be installed in bathrooms or bedrooms does not make sense. Why can't a whole house fan in a mobile home be located in a bathroom? This goes against what is allowed in the ASHRAE standard. |  |  | Accepted | Clarifies SWS and achieves stated objective. | No change | No resistance greater than 3 pascals will exist between fan intake location with reference to the common area | No change
6.6288.1b | Single-Family Homes | Ventilation | Whole Building Ventilation | Special Considerations | Sound-Rating Limits | Intermittent local ventilation system | Local ventilation will be rated for sound at a maximum of 3 sone, unless their maximum rated airflow exceeds 400 cfm CFM Cubic feet per minute , in accordance with ASHRAE ASHRAE American Society of Heating, Refrigerating and Air-Conditioning Engineers, www.ashrae.org 62.2-2010 | Minimize noise | Adjudicated - Redline only | 2015-06-12 | 2015-06-12 | Kelly Cutchin C... | Bring into alignment with other references to 62.2 and avoid maintenance issue of updating document every time a new ASHRAE 62.2 is published. | Local ventilation will be rated for sound at a maximum of 3 sone, unless their maximum rated airflow exceeds 400 cfm, in accordance with current ASHRAE 62.2 standard | No. | Accepted | Brought into line with item 6.6288.1a text. | No change | Local ventilation will be rated for sound at a maximum of 3 sone, unless their maximum rated airflow exceeds 400 cfm, in accordance with current ASHRAE 62.2 standard | No change
7.8003.1a | Single-Family Homes | Baseload | Plug Load | Lighting | Lighting Upgrade | Day lighting | Window coverings (e.g., blinds, shades, moveable insulation) will be replaced or maneuvered to maximize useful daylight where appropriateActive and passive day lighting will be properly oriented, designed, and installed where appropriate | Reduce energy use without negative consequences (e.g., glare, unintentional heating) | Adjudicated - Redline only | 2014-04-23 | 2014-04-23 | Darrel Tenter Tenter | Moveable is misspelled. Should be movable. |  |  | Accepted | Clarifies SWS and achieves stated objective. | No change | Window coverings (e.g., blinds, shades, movable insulation) will be replaced or maneuvered to maximize useful daylight where appropriateActive and passive day lighting will be properly oriented, designed, and installed where appropriate | No change
7.8102.2i | Single-Family Homes | Baseload | Water Heating | Installation and Replacement | Storage-Type Appliance | Thermal efficiency | If additional tank insulation is installed, it will be rated a minimum of R-11 and will be installed to manufacturer specificationsIf additional insulation is installed, it will be installed based on fuel type, making sure not to obstruct draft diverter, pressure relief valve, thermostats, hi-limit switch Hi-limit switch A protective electronic switch that keeps a burner from continuing to operate and damage the appliance , plumbing pipes or elements, and thermostat access platesThe first 6' of inlet and outlet piping will be insulated in accordance with manufacturer specificationsPipe insulation must remain 3'' from gas water heater ventHeat traps will be installed on the inlet and outlet piping where not provided by manufacturer | Reduce standby loss Standby loss Heat loss through the outer part of a water heater. Energy that is used even when a device is turned off from near tank piping and storage tankEnsure insulation does not make contact with flue gas venting | Adjudicated - Redline only | 2015-02-17 | 2015-02-17 | Ken Feller | The minimum distance of 3" to pipe insulation to vent stated here is at least confusing and at worst in conflict with NFPA 211 and the 2012 IRC, Table G2427.10.5. The term "vent" in the IRC is defined as a manufactured device such as "B" vent that uses a clearance specified by the manufacturer. Most often in the field, the clearance issue with pipe insulation is to a "connector" as defined by IRC usually single wall pipe, which in the table cited requires a minimum clearance of 6". Please clarify. | Combustible pipe insulation must maintain a minimum clearance of 6" from gas water heater draft hood andor single wall metal pipe. Clearance from vent such as "B" vent should be maintained per vent manufacturer's specifications. | No. | Accepted with modification | Clarifies SWS and achieves stated objective, made same edits to manufactured housing. | No change | If additional tank insulation is installed, it will be rated a minimum of R-11 and will be installed to manufacturer specifications If additional insulation is installed, it will be installed based on fuel type, making sure not to obstruct draft diverter, pressure relief valve, thermostats, hi-limit switch, plumbing pipes or elements, and thermostat access plates The first 6' of inlet and outlet piping will be insulated in accordance with manufacturer specifications Combustible pipe insulation must maintain a minimum clearance of 6" from gas water heater draft hood and/or single wall metal pipe. Clearance from vent such as "B" vent should be maintained per vent manufacturer's specifications Heat traps will be installed on the inlet and outlet piping where not provided by manufacturer | No change
7.8104.3d | Multifamily Homes | Baseload | Water Heating | Distribution | Piping | Insulation | All piping and fittings will be insulated with fixed insulation to IECC IECC International Energy Conservation Code 2012 or ASHRAE ASHRAE American Society of Heating, Refrigerating and Air-Conditioning Engineers, www.ashrae.org 90.1-2010, at a minimumTanks will be insulated to a minimum of R-12.5Insulation will be protected from damage (e.g., protected from underground water, contact, friction from pipe hangers, woodpeckers, ultraviolet radiation ) | Prevent the pipe from freezingMinimize heat loss from the pipesReduce the risk of moisture damage | Adjudicated - Redline only | 2015-04-22 | 2015-04-22 | Kelly Cutchin C... | N/A | You can delete this comment after reading. Just wanted to point out that we're protecting the insulation from many things, including, specifically, woodpeckers. I wish I'd been on this committee! | No. | Rejected | Rejected per commenter instructions | No change | No change | No change
Note on N64: kelly: less about the technical validity; SWS should be used as if/then, they are not prescriptive measures for EVERYONE to ALWAYS follow
Note on A79: Alison Holm: Classification originally listed as 4.1005.3c. Updated to 4.1005.3e to reflect comments.
Note on N80: NREL: Are there standards for open, medium, dense pack?
Note on N102: NREL: class A is 0-25 flame spread

## Sheet2 (hidden)
Accepted
Accepted with Modifications
Further Investigation Required
Rejected